## Slide 1
July 2023
PRE-EXAM CODE CLASS

## Slide 2
Chief Electrical Inspector
Clint Hansen
402.471.3506
Or
402.440.5739
NEBRASKA STATE ELECTRICAL DIVISION

## Slide 3
OUR LOCATION
1220 LINCOLN MALL, SUITE 125
LINCOLN, NE 68508

## Slide 4
NEBRASKA STATE ELECTRICAL DIVISION

## Slide 5
Sioux
Scottsbluff
Banner
Kimball
Dawes
Box Butte
Morrill
Cheyenne
Sheridan
Garden
Deuel
Cherry
Grant
Hooker
Thomas
Arthur
McPherson
Logan
Keith
Perkins
Chase
Dundy
Lincoln
Hayes
Hitchcock
Frontier
Red
Willow
Keya Paha
Brown
Rock
Blaine
Custer
Dawson
Gosper
Furnas
Boyd
Holt
Garfield
Loup
Wheeler
Valley
Greeley
Sherman
Howard
Buffalo
Phelps
Harlan
Kearney
Franklin
Knox
Antelope
Boone
Nance
Merrick
Hamilton
Hall
Adams
Webster
Clay
Nuckolls
Cedar
Pierce
Madison
Platte
Polk
York
Fillmore
Thayer
Dixon
Wayne
Stanton
Colfax
Butler
Seward
Saline
Jeffer-
son
Dakota
Thurston
Burt
Dodge
Washington
Saunders
Douglas
Sarpy
Lancaster
Cass
Otoe
Gage
Pawnee
Richardson
Nemaha
Johnson
3
2
1
4
8
6
9
10
15
11
7
13
14
5
DISTRICT 1
BRUCE HOFFMAN
308.631.1828
DISTRICT 2
DOUG PARKS
308.530.2783
DISTRICT 3
JOHN MORGAN
402.389.0199
DISTRICT 4
GARY LOFTON
308.325.2219
DISTRICT 5
STUART BAUER
402.461.8574
DISTRICT 6
KIM FARNSTROM
308.750.1841
DISTRICT 7
TODD FLICK
402.649.7730
DISTRICT 8
GREG LASKA
402.649.7742
DISTRICT 9
RON DRUDIK
402.460.0260
DISTRICT 10
ROBERT COLMAN
402.440.5740
DISTRICT 11
DANIEL LOVERCHECK
402.499.5842
DIVISION DIRECTOR
CRAIG THELEN
402.471.3550
DISTRICT 13
DENNIS CARRAHER
402.443.8222
DISTRICT 14
JAMES WILSON
402.499.5841
DISTRICT 15
RALPH QUICK
402.643.0052
DISTRICT 12
CLINT HANSEN
402.471.3506
402.440.5739
CHIEF ELECTRICAL
INSPECTOR
OFFICE
MELISSA HAMILTON
402.471.1358
Allyson Crawford-Thiel
402.471.1058
JULIE SCHROEDER
402.471.3507
Cuming
16
DISTRICT 16
LESLIE SCHNEIDER
531.510.8724

## Slide 6
NEBRASKA STATE ELECTRICAL DIVISION
STATE RECIPROCITY
IMPORTANT FACTS TO
KNOW BEFORE YOU APPLY
FOR RECIPROCITY

## Slide 7
You must have received a 75% or greater on the exam for the license you wish to reciprocate.
You must have held the license you wish to reciprocate in good standing for a period of not less
than one (1) year.
The applicant must have passed a State examination (not a city) in order for the license to reciprocate to another state.
STATE RECIPROCITY

## Slide 8
You must have 4 years registered and 8000 hours work to reciprocate.
If you use school as one of your years of eligibility,
you CAN NOT RECIPROCATE.
The license must be active and not expired.
If the issuing state has no record of your exam it will be rejected.
STATE RECIPROCITY

## Slide 9
ELECTRICAL CONTRACTOR CAN RECIPRICATE WITH:
MINNESOTA
SOUTH DAKOTA
JOURNEYMAN CAN RECIPRICATE WITH:
ALASKA – NORTH DAKOTA – OKLAHOMA – IDAHO
ARKANSAS – MINNESOTA – NEW MEXICO – WYOMING
SOUTH DAKOTA – TEXAS – COLORADO - MONTANA - IOWA
STATE RECIPROCITY

## Slide 10
WHAT IS THE RATIO OF APPRENTICE TO LICENSED ELECTRICIAN ?
81-2113 * The licensee may employ or supervise apprentice electricians at a ratio not to exceed three apprentice electricians to one licensee…

## Slide 11
STATE ELECTRICAL ACT
Rough-in or pre-cover
Re-inspections for Correction Orders
Finals
All of these
According to the State Electrical Act and Board rules, it is the electrical contractor's responsibility to call the inspector to schedule which of the following types of inspections during the coarse of the project?
ALL OF THESE

## Slide 12
RULE NUMBER 14
Requests for Inspection
It shall be the responsibility of the installer or electrical contractor to notify the inspector at such times as the project is ready for inspection.
As used in this rule, “ready for inspection” shall mean (1) rough-in inspections necessary prior to the concealment of wiring, and (2) final inspections, and (3) re-inspection required by the issuance of a “correction order”. The requirement of timely notification is an ongoing responsibility of the installer or electrical contractor during the entire life of the project.
Notification shall be made by telephone request or written request to the State Electrical Division or area State Electrical Inspector.

## Slide 13
PRACTICAL SAFEGUARDING
This Code is not intended as a design specification or an instruction manual for untrained persons.
The purpose of this Code is the practical safeguarding of persons and property from hazards arising from the use of electricity.
Adequacy
This Code contains provisions that are considered necessary for safety.
90.1 PURPOSE
NATIONAL ELECTRICAL CODE

## Slide 14
CHAPTER 1 - General
CHAPTER 2 – Wiring and Protection
CHAPTER 3 – Wiring Methods and Materials
CHAPTER 4 – Equipment for General Use
90.3 CODE ARRANGEMENT
Chapters 1 through 4 generally apply to all applications

## Slide 15
CHAPTER 5 – Special Occupancies
CHAPTER 6 – Special Equipment
CHAPTER 7 – Special Conditions
Chapters 5 through 7 can supplement or modify the general requirements of Chapters 1 through 7
90.3 CODE ARRANGEMENT

## Slide 16
CHAPTER 8 – Communications Systems
Chapter 8 requirements aren’t subject to requirements in Chapters 1 – 7 unless there’s a specific reference in Chapter 8 to a rule in
Chapters 1 through 7.
CHAPTER 9 – Tables
Chapter 9 tables are applicable as referenced in the NEC and are
used for calculating raceway sizes, conductor fill, and voltage drop.
Informative Annex A through Informative Annex J
These are informational only and not mandatory.
90.3 CODE ARRANGEMENT

## Slide 17
INFORMATIVE ANNEX H

## Slide 18
INFORMATIVE ANNEX H

## Slide 19
INFORMATIVE ANNEX H

## Slide 20
115 percent
125 percent
140 percent
150 percent
The disconnecting means for a torque motor shall have an ampere rating of at least what percentage of the motor nameplate current?
The correct Answer would be A.
Section 430.110(B) requires the disconnecting means for a torque motor to have an ampere rating of at least 115 percent of the motor nameplate current.
The question is about motor disconnecting means
In the index find “Motors” and find “Disconnecting Means, 430.95, 430-IX.”
Scan Article 430-Part IX and find 430.110, Ampere Rating and Interrupting Capacity.

## Slide 21
15.2 amperes
16.7 amperes
28.0 amperes
30.8 amperes
The full load current rating of a 5-horsepower, single-phase, 208-volt motor is:
The correct Answer would be D.
Table 430.248 specifies a full-load current of 30.8 amperes for the specified motor.
The question is about full-load current ratings of motors.
In the index find “Motors” and find “Current, full load. See Full-lad current motors.” In Index, find “Full-load current motors,” find “alternating current, Single-phase, Table 430.248.”
Note: Section 430.6(A)(1) requires that this value be used to size the components of the motor circuit, except the motor overload protection, which must be based on the actual motor nameplate ampere rating. Overload
protection is found in Part III of Article 430. The full load current value in amperes from the table will normally be higher than the ampere rating on the nameplate.

## Slide 22
14 AWG
12 AWG
10 AWG
8 AWG
Which one of the following is the minimum permitted size of Type THW copper branch-circuit conductors
supplying a continuous duty motor with a full-load
current value of 40 amperes determined from
Tables 430.247 – 250?
Assume all terminations are rated 75oC.
The correct Answer would be D.
Section 430.22 requires branch-circuit conductors supplying a single motor in a continuous
duty application to have an ampacity not less than 125 percent of the motor full-load current rating as determined by 430.6(A)(1).
The question is about sizing motor branch-circuit conductors.
In the index find “Motors” and find “Branch circuits, 430-Part II.” Scan“Part-II, Motor Circuit Conductors,” find “430.22, Single Motor.”
125% x 40 A = 50 amps, which is the minimum ampacity of motor branch-circuit conductors
Referring to ampacity Table 310.15(B)(16), 8 AWG Type THW copper is rated 50 amperes, with
75oC terminals, while the next smaller size 10 AWG, is only rated at 35 amperes.

## Slide 23
1
2
3
4
The minimum number of overload units
providing overload protection for a 3-phase
ac motor connected to a 120/208-volt,
3-phase, 4-wire system is:
The correct Answer would be C.
Table 430.37 requires three devices, one in each phase.
The question is about requirements for motor overload units.
In the index find “Motors” and find “Three overload units, Table 430.37.”

## Slide 24
OHM’S LAW I=V/R
VOLTAGE
Represented by
V or E
Voltage:
a force that pushes the current through the circuit.
CURRENT
Represented by
I
Current:
the actual substance” that is flowing through the wires of the circuit.
RESISTANCE
Represented by
R
Resistance:
Friction that impedes flow of current through the circuit.
WATTS
Represented by
VA or P
A watt is a measure of electrical power which is the product of multiplying the applied voltage (or potential) by the amperage (or current).

## Slide 25
1.60V
3.20V
6.40V
12.80V
What is the voltage drop of two 12 AWG
conductors (0.40ohms) supplying a 16A load,
located 100 ft. from the power supply?
Formula: E = I x R
The correct Answer would be C.
E = 16A x 0.40 ohms
E = 6.40V
The question is about voltage drop.
So we take the formula E=IxR and put in the values

## Slide 26
0.14 ohms
0.30 ohms
3 ohms
14 ohms
What is the resistance of the circuit conductors when the conductor voltage drop is 7.20V and the current flow is 50A?
The correct Answer would be A.
R=7.20V/50A
R= 0.14 ohms
The question is about resistance of circuit conductors.
So we take the formula R = E/I and put in the values

## Slide 27
175W
350W
700W
2,400W
What is the power loss in watts of a conductor that carries 24A and has a voltage drop
of 7.20V?
The correct Answer would be A.
P = 24A x 7.20V
P = 172.80 W
The question is about power loss in watts of conductors.
So we take the formula P = I x E and put in the values

## Slide 28
8.2 kW
9.5 kW
11.3 kW
12.4 KW
What is the approximate power consumed by a 10 kW heat strip rated 230V, when connected to a 208V circuit?
The power of the heat strip will be less because the applied voltage (208V) is less than the
equipment voltage rating (230V). To calculate this, we must determine the heat strip resistance rating at 230V, and then determine the power rating at 208V based on the heat strip resistance rating.
The question is about the approximate power consumption by heat strip.
So we take the formula P = I x E and put in the values

## Slide 29
8.2 kW
9.5 kW
11.3 kW
12.4 KW
What is the approximate power consumed by a 10 kW heat strip rated 230V, when connected to a 208V circuit?
P = E2/R
P = (208V x 208V)/5.29 ohms
P = 43,624/5.29 ohms
P = 8,178W/1,000
P = 8.20 kW
P = E2/R
E = Applied Voltage = 208V
R = Resistance of Heat Strip = E2/P
Heat Strip Voltage Rating = 230V
Power Rating of Heat strip = 10,000W
Resistance of Heat Strip = 230V2/10,000W
Resistance of Heat Strip = 5.29 ohms

## Slide 30
$30
$50
$70
$90
What does it cost per year (at 8 cents per kWh) for the power loss of a 12 AWG circuit conductor (100 ft. long) that has a total resistance of
0.40 ohm and current flow of 16A?
Cost per year = Power for the year in kWh x $0.08
Power per hour = I2 X R
I = 16A
R = 0.40 ohms
Power per hour = (16A x 16A) x 0.40 ohms
Power per hour = 102.40W
Power for the year in kWh = (102.40W x 24 hours x 365 days)/1,000
Power for the Year in kWh = 897 kWh
Cost per year = 897 kWh x $0.08
Cost per year = $71.76
Answer would be C.

## Slide 31
Where the conductors terminate in a single overcurrent device and are not over 7.5 m (25 ft.) in length
Where the design and operation of the generator prevent overloading
Where the load supplied is all non-continuous
Where the rating of the generator does not exceed the short-circuit rating of the device supplied
The conductors from a generator to the first
overcurrent device are not required to be sized larger than the nameplate rating of the generator under
which one of the following conditions?
The correct Answer would be B.
Section 445.13 requires conductors from the generator terminals to the first overcurrent
device to be sized 115% of the nameplate current rating.
The question is about the ampacity of conductors from a generator.
In the index find “Generators” and find “Conductor, ampacity of, 445.13.”
The Exception to Section 445.13 permits the ampacity of the conductors to be not less than 100%
of the nameplate current rating of the generator where the design and operation of the generator prevent overloading.

## Slide 32
4 circuits
5 circuits
7 circuits
8 circuits
How many 20A, 120V circuits are required for
forty-two, 300W luminaires (noncontinuous
load) that have a power factor of 85 percent?
VA per Circuit = Volts x Amperes
VA per Circuit = 120V x 20A
VA per Circuit = 2,400 VA
Lights per Circuit = 2,400 VA/ 353 VA = 6.80
Lights per Circuit = 6
Circuits = 42 luminaires/ 6 per circuit
Circuits = 7
The Answer is C.
VA per Luminaire = Watts/Power Factor
VA per Luminaire = 300W/ 0.85 PF
VA per Luminaire = 353 VA

## Slide 33
5 seconds
10 seconds
15 seconds
20 seconds
Where the generator is used to provide alternate
power for the life safety and critical branches system
in a hospital, the transfer time from normal power to emergency power for the life safety branch shall be a maximum of:
The correct Answer would be B.
Section 517.32 addresses branches requiring automatic connection. Section 517.32(B)
requires the life safety and critical branches of the essential system to be restored to
operations within a maximum of 10 seconds transfer time.
The question is about generator transfer time for a hospital life-safety branch.
In the index find “Health care facilities” and find “Essential electrical systems, 517 Part III.”
then find “Critical Branch, 517.32

## Slide 34
51A
58A
65A
80A
What is the nameplate FLA for a 20 hp, 208V,
three-phase motor with 90 percent power factor and 80 percent efficiency?
FLA = (Motor hp x 746W)/(E x 1.732 x PF x EF
FLA =(20 HP X 746w)/(208V x 1.732 x 0.9 PF x 0.80 Eff)
FLA = 58A
The Answer is B.

## Slide 35
Armature leads
Series circuit
Compound winding on the armature
Shunt field
A 2-wire dc generator may have an overcurrent device in any of the following EXCEPT the:
The correct Answer would be D.
Section 445.12(B), Two-Wire Generators, provides that the overcurrent device shall not open
the shunt field.
The question is about overcurrent protection for 2-wire generators.
In the index find “Generators” and find “Overcurrent protection, 445.12.”

## Slide 36
100 amperes
115 amperes
125 amperes
150 amperes
The maximum ampacity of the phase conductors from the
terminals of a 100-ampere-rated generator, which is not
designed to prevent overloading to the first overcurrent
device, shall not be less than how many amperes?
The correct Answer would be B.
Section 445.13 requires the ampacity of the phase conductors from the generator terminals to the
first overcurrent device(s) to be not less than 115 percent of the nameplate current rating of the
generator
The question is about the ampacity of conductors from the generator to the first overcurrent device.
In the index find “Generators” and find “Conductor, ampacity of, 445.13.”
Section 445.13 applies, as the exception is not specifically addressed in the question.
115% x 100 amperes =115 amperes.

## Slide 37
75W
100W
300W
600W
The total circuit resistance of two 12 AWG
conductors (each 100 ft. long) is 0.40 ohms.
If the current of the circuit is 16A, what is the power loss of the conductors in watts?
P = I2 x R
I = 16A
R = 0.40 ohms
P = (16A x 16A) x 0.40 ohms
P = 102.40W
Answer would be B.

## Slide 38
50 percent
80 percent
100 percent
125 percent
A direct-current generator neutral conductor that must
carry ground-fault currents shall not be smaller than
what percentage of the size of the largest phase
conductors?
The correct Answer would be C.
In 445.13, the last sentence requires the neutral conductor not to be smaller than the
minimum required size of the largest phase conductor.
The question is about sizing neutral conductors for generators.
In the index find “Generators” and find “Conductor, ampacity of, 445.13.”

## Slide 39
Be omitted
Be interlocked
Be connected to an annunciator
Interrupt the generator field circuit
If the authority having jurisdiction deems the generator set is vital to the operation of an electrical system,
instead of interrupting the generator circuit, the
overload sensing device may:
The correct Answer would be C.
Section 445.12, Exception to (A) through (E), indicates where all the conditions are met, the
overload sensing device may be connected to an annunciator or alarm supervised by
authorized personnel instead of interrupting the generator circuit.
The question is about means to interrupt current to the generator circuit.
In the index find “Generators” and find “Overcurrent protection, 445.12.”
The phrase which is vital to operation of an electrical system has a sense of urgency or
exception to the rule.

## Slide 40
Pressure relief
A flame arrester
Fluid level indicators
None of these
Each vented cell of a battery, as it relates to
storage batteries, shall be equipped with ____that prevents destruction of the cell due to
ignition of gases within the cell by an external spark or flame.
The question is about vented cell batteries
In the index look up “batteries” you need to go to “Storage batteries” and find vents.
It directs you to 480.11
480.11(A) states that they shall be equipped with a flame arrester.
The answer will be B.

## Slide 41
A room fully protected by an automatic water sprinkler system
A room fully protected by an automatic carbon dioxide fire protection system
A room with a 1-hour fire rating
A nonfire-rated electrical equipment room
A generator supplying the emergency system in a
30.0 m (100 ft.) high apartment building may be
installed in any of the following locations EXCEPT:
The correct Answer would be D.
Section 700.12(B) does not provide any information for the question, so scan 700.12.
The question is about the location of emergency generators.
In the index find “Generators” and find “Emergency systems, 700.12(B).”
The fourth paragraph of 700.12 requires that emergency sources of power described in
700.12(A) through (E), which includes generators, to be installed in spaces fully protected by
approved automatic fire suppression systems (sprinklers, carbon dioxide, and so forth) or in
spaces with a 1-hour fire rating where (2) located in buildings (including residential)
above 23.0 m (75 ft.) in height.

## Slide 42
Separate sleeve or tube
Weatherproof tube
Tube of absorbent material
Grounded metallic tubing
A conductor used for open wiring on insulators that penetrates a wall, floor, or other framing member shall be carried through a _____.
The question is about open wiring conductors
In the index look up “Open wiring on insulators” then look at “through or parallel to
framing members.
It directs you to 398.17
398.17 says that each conductor shall be carried through a “separate sleeve or tube”
The answer will be A.

## Slide 43
150 percent
175 percent
225 percent
400 percent
Where motor branch-circuit short-circuit and ground fault
protection is provided by time-delay (dual-element) fuses
and their rating specified in Exception 1 is not sufficient to
start the motor, it shall be permitted to increase their rating
to what percentage of the full-load current rating of the
motor, (while not exceeding standard ampere ratings of overcurrent devices)?
The correct Answer would be C.
Section 430.52(C)(1) states the protective device rating cannot exceed the values permitted in Table 430.52. Ex. # 2(b) to Table 430.52 allows a time-delay fuse to be increased to no more
than 225 percent of the full-load current of a motor where the rating specified in Table 430.52 or the rating modified by EX. #1 is not sufficient to start the motor.
The question is about the rating of the motor branch-circuit short-circuit and
ground-fault protection.
In the index find “Motors” and find “Rating or setting of branch-circuit short-circuit and
ground-fault devices Table 430.52.”

## Slide 44
10A or less
15A or less
15A or more
20A or less
Pilot lights, instruments, voltage (potential)
transformers, and other switchboard devices
with potential coils shall be supplied by a
circuit that is protected by standard
overcurrent devices rated______.
The question is about protection of instrument circuits in a switchboard
In the index look up “Panelboards” then look at “overcurrent devices”
It directs you to 408.36, 408.52, 408.54, 408.36 Ex. 1
If you scan through those sections you will see 408.52 addresses the instrument circuits.
The answer will be B.

## Slide 45
150V
250V
300V
600V
The maximum voltage permitted between
ungrounded conductors of flat conductor cable systems is ______.
The question is about maximum voltage of flat conductor cables.
In the index look up “Flat cable cables” then look at “branch circuit ratings”
It directs you 324.10(B)(1)
If look at 324.10(B)(1) it shall not exceed 300V
The answer will be C.

## Slide 46
Calculations
THE STANDARD CALCULATION CAN BE EASILY CALCULATED WHEN YOU FOLLOW THE FOLLOWING STEPS.
FIRST – Calculate the general lighting load
SECOND – Calculate the appliance loads and motor loads
LAST – Add the results from the first three steps for the total
THIRD – Calculate 25% of the largest motor

## Slide 47
Calculations
In an office building with 2500 square feet, the number of general purpose
receptacle outlets to be installed equals 14.
So what load in VA is used to calculate the receptacle load for this office building ?
What code section(s) are we going to use?
We need to use the larger of:
Answer: 2520 VA
(1) - 14 X 180 VA = 2520 VA
Table 220.12 (footnote (b)) and 220.14(K)
or (2) - 2500 sq. ft. X 1 VA = 2500 VA

## Slide 48
Calculations
A 120/240 V, single phase, 3 wire feeder will supply 100 general purpose
receptacles in an office building with 12,500 sq. ft.
What is the minimum calculated load to be used for sizing the feeder?
What code section(s) are we going to use?
100 X 180 VA = 18,000 VA
-10,000 VA @ 100% = 10,000 VA
14,000 VA / 240V = 58A
8000 VA @ 50% = + 4,000 VA
220.14(I) and Table 220.44
from Table 220.44
14,000 VA

## Slide 49
Calculations
How many 120V, 2-wire, 20A branch circuits are required to supply 52 parking lot lights rated at 500VA each and are continuous load?
What code section(s) are we going to use?
500VA X 1.25 = 625VA (continuous load)
52 lights / 3 lights per circuit = 17.33 or 18 circuits required
625VA / 120V = 5.208A per light
210.20(A)
from 210.20(A)
20A per circuit / 5.208A per light = 3.84 lights per circuit
OHM’S LAW

## Slide 50
Calculations
A single family dwelling, supplied by a 120.240V, single phase service.
It has 3200 sq. ft. and the following equipment:
15KVA fixed space heater at 240V
14,000VA range at 240V
6,000VA clothes dryer at 240V
1,000VA disposal motor at 120V
1,500VA fan motor at 240V
(5) non-motor appliances, fastened in place, with a total combined nameplate
rating of 10,500VA.
Using the standard calculation method, without exceptions, calculate the total load in VA for this single family dwelling.
START WITH GENERAL LIGHTING

## Slide 51
Calculations
GENERAL LIGHTING
3200 X 3VA per sq. ft. = 9600VA
2 Small Appliance = 3000VA
1 Laundry = 1500VA
14100VA
220.12
210.52(B)
First 3000VA@100% = -3000VA
11100VA
Table 220.42
220.52(A)
Table 220.42
Remainder @35% = X .35 .
3885VA
Total General Lighting Load = 3000VA + 3885VA = 6885VA

## Slide 52
Calculations
Derated Appliances 15000VA HEAT
8800VA RANGE
6000VA DRYER
1000 X .75 = 750VA DISPOSAL
1500 X .75 = 1125VA FAN MOTOR
10500 X .75 = 7875VA OTHER FASTENED APP
39550VA
220.53
220.53
TOTAL DERATED APPLIANCE LOAD = 39550VA
220.51
220.55
220.54
220.53

## Slide 53
Calculations
LARGEST MOTOR 1000VA / 120V = 8.3A (LARGEST MOTOR)
1500VA / 240V = 6.25A
1000VA X .25 = 250VA (25% of Largest motor)
ANSWER IS 6885 + 39550 + 250 = 46685VA
220.50

## Slide 54
Receptacle outlets are required in all of the following
locations at a single-family residence EXCEPT:
  The question is about locations where receptacles are required at single-family dwellings
Sections 210.52(E), Outdoor Outlets, 210.52(G), Basements, Garages and Accessory Buildings,
and 210.52(H), Hallways, require a receptacle in locations A, C, and D above
Basements
Underfloor space used for storage
Hallway that is 3.0 m (10 ft.) or longer
Outdoors at front and back at grade level
In Index, find “Receptacles…” under which find “Outlets” under which find “Dwellings, where
required, 210.52.”
The correct answer is B.
There is no specific requirement for a receptacle outlet in an underfloor space used for storage

## Slide 55
2,000 amps
1,500 amps
1,800 amps
1,600 amps
A 120/240-volt, single-phase, 3-wire service is installed. Using the standard
calculation method, what is the calculated service size in amperes for a
multifamily dwelling having 40 dwelling units with 1000 square feet each with a 8 kVA range; 1.2 KVA dishwasher; 0.6 kVA disposer; 0.5 kVA instant hot
water appliance; 120-volt, single-phase A/C at 18 amps; and a 2.5 kVA
240-volt water heater, and a 2.5 kVA 240-volt heater. (House and laundry loads are not
included.)
Section 230.42(A) requires that the conductors shall be of sufficient size to carry the loads as computed in accordance with article 220.
The question is about calculating the service-entrance size for a multifamily residential
building. Note that the laundry loads – a clothes washer and clothes dryer – are not included for each unit. There may be a separate “laundry room” with coin-operated machines,
possibly, which may even be located on-site in a separate building; but we don’t know
anything except that the laundry loads are not included. Also be aware that there is no
requirement in the NEC that the owner of the building install these, though laundry facilities in the apartment are a feature that many tenants look for as a convenience.
In the index find “Service-entrance conductors” find “Size, 230.42

## Slide 56
Kitchen small appliance [210.11(C)(1) & 220.52(A)]
Load =1500 VA x 2 circuits x 40 units
Load =120,000 VA Total general lighting and small appliance load
A 120/240-volt, single-phase, 3-wire service is installed. Using the standard
calculation method, what is the calculated service size in amperes for a
multifamily dwelling having 40 dwelling units with 1000 square feet each with a 8 kVA range; 1.2 KVA dishwasher; 0.6 kVA disposer; 0.5 kVA instant hot
water appliance; 120-volt, single-phase A/C at 18 amps; and a 2.5 kVA
240-volt water heater, and a 2.5 kVA 240-volt heater. (House and laundry loads are not
included.)
General lighting [220.12]
VA =1000 sq. ft. x 3 VA
Load =3000 VA x 40 units
Load =120,000 VA
Total =general lighting load + kitchen load
=120,000 + 120,000
=240,000 VA
Proceed with the calculations, and calculate the general lighting and small appliance loads
per Sections 220.12, 220.14(J), and 210.11(C)(1), 220.42, and 220.52(A).

## Slide 57
A 120/240-volt, single-phase, 3-wire service is installed. Using the standard
calculation method, what is the calculated service size in amperes for a
multifamily dwelling having 40 dwelling units with 1000 square feet each with a 8 kVA range; 1.2 KVA dishwasher; 0.6 kVA disposer; 0.5 kVA instant hot
water appliance; 120-volt, single-phase A/C at 18 amps; and a 2.5 kVA
240-volt water heater, and a 2.5 kVA 240-volt heater. (House and laundry loads are not
included.)
First 3000 at 100%
=3000 VA
3001 VA to 120,000 VA at 35% (117,000)
=40,950 VA
Remaining over 120,000 VA at 25%
120,000 x .25 = 30,000 VA
Net general lighting load & small appliance load
=3000 VA + 40,950 VA + 30,000 VA
=73,950 VA
Section 220.52(A) permits Table 220.42 demand factor to be applied to this load.

## Slide 58
A 120/240-volt, single-phase, 3-wire service is installed. Using the standard
calculation method, what is the calculated service size in amperes for a
multifamily dwelling having 40 dwelling units with 1000 square feet each with a 8 kVA range; 1.2 KVA dishwasher; 0.6 kVA disposer; 0.5 kVA instant hot
water appliance; 120-volt, single-phase A/C at 18 amps; and a 2.5 kVA
240-volt water heater, and a 2.5 kVA 240-volt heater. (House and laundry loads are not
included.)
Dishwashers at 1.2 kVA x 40 units =48,000
Disposer at 0.6 kVA x 40 units =24,000
Water heater at 2.5 kVA x 40 units =100,000
Instant-hot water appliance
.5 kVA x 40 units =20,000
Gross appliance load =192,000 VA
Net Appliance Load (220.53) =192,000 VA x 75%
=144,000 VA
Ranges (Table 220.55) Note 3
40 Ranges = 8kVA x 40 x .22 =70,400Va
Calculate the net appliance load per 220.53

## Slide 59
A 120/240-volt, single-phase, 3-wire service is installed. Using the standard
calculation method, what is the calculated service size in amperes for a
multifamily dwelling having 40 dwelling units with 1000 square feet each with a 8 kVA range; 1.2 KVA dishwasher; 0.6 kVA disposer; 0.5 kVA instant hot
water appliance; 120-volt, single-phase A/C at 18 amps; and a 2.5 kVA
240-volt water heater, and a 2.5 kVA 240-volt heater.(House and laundry loads are not
included.)
Calculate the additional 25% for the largest motor load per section 220.14(C), 220.50,
430.22, and 430.24
25% largest motor (220.50) Disposal = 0.6 kVA x .25 =150 VA
Calculate the larger of the heating or cooling loads per Sections 220.14(A), 220.51, and 220.60
40 air conditioners at 18A x 120V =2160 VA x 40 =86,400 VA
40 2.5 kVA 240-volt heaters: =40 x 2.5 =100,000 VA
Section 220.60 states that we are permitted to use only the larger of the two noncoincident
loads, which is the heat load, because the heat and air conditioning will not be operating at the same time

## Slide 60
A 120/240-volt, single-phase, 3-wire service is installed. Using the standard
calculation method, what is the calculated service size in amperes for a
multifamily dwelling having 40 dwelling units with 1000 square feet each with a 8 kVA range; 1.2 KVA dishwasher; 0.6 kVA disposer; 0.5 kVA instant hot
water appliance; 120-volt, single-phase A/C at 18 amps; and a 2.5 kVA
240-volt water heater, and a 2.5 kVA 240-volt heater. (House and laundry loads are not
included.)
In the index, find “Overcurrent Devices” under which find “Standard; 240.6” In 240.6, we
find that a 2,000-amp overcurrent device is the closest standard rating to a 1,619-ampere load.
Add the sum of all of the net computed lighting, appliance, range, heating or cooling loads,
and 25% of the largest motor load.
Sum =73,950 VA + 144,000 VA + 70,400 + 100,000 VA + 150 VA
Sum =388,500 VA
=388,500 VA ÷ 240 V = 1,619 amperes.
NOTE: A 2000-ampere rated service disconnecting means is required. The service
conductors would also be required to be sized for 2000 amperes as we are not permitted to round up to the next standard overcurrent device 2000 amperes) from the 1,619
calculated load. Section 240.6 does not permit rounding up over 800 amperes in other
than specific industrial applications
The correct answer is A 2,000 amperes

## Slide 61
Which of the following wiring methods is NOT permitted in a Class I, Division 1 hazardous (classified) location?
  The question is about wiring methods permitted in Class I, Division 1 hazardous (classified)
  locations.
Scan Section 501.10(A)(1) and find that answers (A) through (C) are permitted wiring methods.
Threaded rigid metal conduit
Threaded steel intermediate metal conduit
Type MI cable with appropriate termination fittings
Type MC cable
In Index, find “Hazardous (Classified) Locations, ClassI” under which find “Wiring methods,
501.10.”
The correct answer is D.
Scan Section 501.10(A)(1) and find Type MC-HL cable is permitted in limited locations provided it has specific construction specifications, but standard type MC cable is not permitted.

## Slide 62
Without considering any exceptions, what is the general lighting load of an office building with an area of 4500
square feet and the actual number of general-purpose
receptacle outlets is unknown?
The question is about the calculation of branch-circuit lighting loads.
In the index, find “Branch circuits” under which find “Calculation of loads, 220 Part II, and Annex D.” You can find “Lighting” in the Index under which find “Branch circuits,
calculation of load, 220.12”
Section 220.12, Lighting Loads for Specified Occupancies, refers to Table 220.12.
13,500 VA
15,750 VA
18,000 VA
20,250 VA
Proceed with the calculations.

## Slide 63
Without considering any exceptions, what is the general lighting load of an office building with an area of 4500
square feet and the actual number of general-purpose
receptacle outlets is unknown?
  Lighting load [Table 220.12]
  = 4500 sq. ft. x 3.5 VA per sq. ft.
  = 15, 750 VA
Receptacle outlets [Superscript Note b to Table 220.12 refers to 220.14(K)] Section 220.14(K) requires the larger of 220.14(k)(1) or (2). Because the actual number of receptacles is
unknown, 220.14(K)(2) is chosen.
= 4500 sq. ft. x 1.0 VA per sq. ft.
= 4500 VA
Total = 15,750 + 4500 = 20,250 VA
13,500 VA
15,750 VA
18,000 VA
20,250 VA
The correct Answer is D.

## Slide 64
What is the minimum ampacity for a 480Y/277-volt,
3-phase, 4-wire feeder supplying a 150 kVA fixed
electric space heating load?
  The question is about the minimum calculated feeder load for fixed electric space heating.
Section 215.2(A)(1)(a) generally requires feeders to be able to carry 100% of the
non-continuous load and 125% of the continuous load. Section 220.40 requires feeder
conductors to have sufficient ampacity to supply the load served and in no case shall the
computed load of a feeder be less than the total computed branch-circuit load per Part II after demand factors of Parts III, IV or V have been applied.
181 amperes
226 amperes
313 amperes
391 amperes
Scan Part II and find “220.51, Fixed Electric Space Heating,” which requires the feeder load to be calculated at 100% of the total connected fixed electric space-heating load.
In Index, find “Feeders” under which find “Calculation of loads, see Loads.” Under “Loads,”
find “Feeders, calculations, 215.2(A), Article 220, and Annex D.”

## Slide 65
What is the minimum ampacity for a 480Y/277-volt,
3-phase, 4-wire feeder supplying a 150 kVA fixed
electric space heating load?
  Based on the previous, the total feeder load is 150 kVA x 1000 = 150,000 VA at 100%
The correct answer is A, 181 amperes. We will round up from 180.7 amps per 220.5(B).
181 amperes
226 amperes
313 amperes
391 amperes
The minimum conductor ampacity for the 3-phase load is: Use Ohm’s Law Formula:
I (amps) = VA / E (volts) x 1.73 (3-phase)
I = 150,000 / (480 x 1.73)
I = 150,000 / 830.4
I = 180.7 amperes

## Slide 66
Separate vertical switchgear sections.
Individual disconnects in separate enclosures used to separate emergency loads from all other loads
Neither A nor B
Both A and B
Wiring from a single generator, or multiple generators
operating in parallel, supplying emergency and other
loads shall be permitted to supply which of the following equipment:
The correct Answer would be D.
The question is about the type of equipment which can be supplied by the wiring from
single or multiple generators operating in parallel that are supplying emergency loads as well as other loads.
In the index find “Emergency systems” find “Wiring, 700.10, IN Fig. 700.10(B)(5)(b)(1),
IN 700.10(B)(5)(b)(2)
Looking at 700.10(B) we find the provisions are related to separating emergency loads from
other loads. Section 700.10(B)(5)(a) addresses the type of equipment that can be supplied
from an emergency source and permits wiring from an emergency source supplying other
loads to supply separate vertical switchboard sections or individual disconnects in separate
enclosures.

## Slide 67
A dwelling unit has three electric wall-mounted ovens rated
8.0, 6.0, and 3.5 kVA respectively; a counter-mounted
cooking unit (cooking unit (cook top) rated at 6.0 kVA; and a counter-mounted broiler at 3.5 kVA. The calculated demand
load is:
  The question is about the calculated demand load of cooking appliances in a dwelling unit
  supplied by a 120/240 single phase, 3-wire, dwelling unit service.
Section 220.55 permits the load for our electric cooking appliances rated greater than 1 ¾ kW
and located in a dwelling unit or household cooking appliances used in instructional programs
to be calculated in accordance with Table 220.55. As with the use of any NEC Table we have to pay special attention to any applicable notes. Note 3 permits the nameplate ratings for all
household electric cooking appliances rated more than 1 ¾ kW but not more than 8 ¾ kW to be added together and subjected to the demand factors of Column A or B as applicable.
12.2 kVA
18.6 kVA
27.3 kVA
29.7 kVA
In Index, find “Ranges” under which find “Branch circuits” under which find “Calculation of
load, 220.55 and Table 220.55.”

## Slide 68
A dwelling unit has three electric wall-mounted ovens rated
8.0, 6.0, and 3.5 kVA respectively; a counter-mounted
cooking unit (cooking unit (cook top) rated at 6.0 kVA; and a counter-mounted broiler at 3.5 kVA. The calculated demand
load is:
  We will use the demand factors from Column B for the given number of appliances as they are all rated 3 ½ kW but not more than 8 ¾ kW.
  =8.0 + 6.0 + 3.5
  =27 kVA
The correct answer is A, 12.2 kVA
12.2 kVA
18.6 kVA
27.3 kVA
29.7 kVA
Column B permits a demand of 45% to be applied.
= .45 x 27 kVA
= 12.15 or 12.2 kVA

## Slide 69
What is the minimum size Type THWN copper conductor required for a feeder supplying ten 12 kVA electric
ranges (240-volt, single-phase) in a restaurant kitchen?
  The question is about calculation of feeder loads for electric ranges in a restaurant.
Section 220.56 permits the load for commercial kitchen equipment to be in accordance with
Table 220.56.
2 AWG
1 AWG
350 kcmil
400 kcmil
In Index, find “Kitchen equipment, commercial, 220.56, 422.11(F)(2).”
Proceed with the calculation.
10 appliances x 12 kVA = 120 kVA
65% x 120 kVA = 78 kVA or 78,000 VA
78,000 VA / 240 V = 325 amperes

## Slide 70
What is the minimum size Type THWN copper conductor required for a feeder supplying ten 12 kVA electric
ranges (240-volt, single-phase) in a restaurant kitchen?
  Refer to Table 310.15(B)(16) and find that a 400-kcmil Type THWN CU conductor = 335 amperes and a 350-kcmil Type THWN CU conductor has an ampacity of 310 amperes.
The correct answer is D, 400 kcmil
2 AWG
1 AWG
350 kcmil
400 kcmil

## Slide 71
The classification of Class I, Zone 0, 1, or 2 locations
shall be performed by which one of the following?
  The question is about who is responsible for classifying Class I, Zone 0, 1, or 2 locations.
Scan Section 505.7 and find “505.7(A), Implementation of Zone Classification System.”
A qualified registered professional engineer
The authority having jurisdiction
The owner of the facility
A qualified person
In Index, find “Hazardous (classified) locations, Class I, Zone 0, 1, and 2 locations” under which
find “Special precaution, 505.7.”
The correct answer is D.
Section 505.7(A) requires that the area classification, wiring, equipment selection and
inspections be performed by a qualified person. Supervision by a registered professional
engineer is no longer required.

## Slide 72
All of the following statements regarding individual unit equipment for emergency illumination are true EXCEPT:
  The question is about unit equipment used for emergency lighting.
Section 700.12(F), Unit Equipment, provides the requirements for the type of equipment addressed in the question. Sections 700.12(F)(2)(1) through (3) address the statements in the question including requiring the unit equipment to be connected ahead of local
switches so Answer D is not true.
The unit may be supplied with flexible cord not exceeding 3 ft. in length.
The circuit feeding the unit shall also feed normal lighting in the area.
The unit shall be permanently fixed in place.
The unit may be connected on the load side of local switches.
In Index, find “Emergency systems” under which find “Unit Equipment, 700.12(F).”
The correct answer is D.

## Slide 73
What is the feeder neutral current for a multifamily dwelling fed with a 120/240-volt, single-phase, 3-wire service with a computed load (including demand factors as per Table
220.42) of 111,450 VA including a 40 kVA range load per
Table 220.55?
  The question is about the load on a feeder neutral conductor.
Section 220.61(B)(1) permits the unbalanced neutral load to be considered as 70% of calculated range load with a further demand factor of 70% permitted for that portion of the feeder load in excess of 200 amps permitted in 220.61(B)(2).
351 amperes
432 amperes
485 amperes
500 amperes
In Index, find “Neutral” under which find “Feeder load, 220.61.”
Calculate the amperage of the respective loads.

## Slide 74
What is the feeder neutral current for a multifamily dwelling fed with a 120/240-volt, single-phase, 3-wire service with a computed load (including demand factors as per Table
220.42) of 111,450 VA including a 40 kVA range load per
Table 220.55?
351 amperes
432 amperes
485 amperes
500 amperes
Total feeder load of 111,450 volt-amperes less range load of 40,000 = 71,450 VA. Converting
the volt-ampere loads to amperes:
A = 71,450 VA / 240 volts
A = 298 amperes
A = 40,000 VA (range load) / 240 volts
A = 167 amperes
Calculate the amperage of the respective loads.

## Slide 75
What is the feeder neutral current for a multifamily dwelling fed with a 120/240-volt, single-phase, 3-wire service with a computed load (including demand factors as per Table
220.42) of 111,450 VA including a 40 kVA range load per
Table 220.55?
70% of 167 A (range load) = 117 amps
Total Neutral Load = general neutral load plus range neutral load (including demand factor)
= 298 amps + 117 amps
= 415 amps
351 amperes
432 amperes
485 amperes
500 amperes
And per 220.61(B)(2):
100% of the first 200 A = 200 amperes
70% of load in excel of 200 A = 415 A – 200 A = 215 A
=215 A X 70% = 151 A
= 151 A + 200 A
Total Neutral Demand Load = 351 amperes
The correct answer is A, 351 amperes.

## Slide 76
Which one of the following is not a standard rating for a branch circuit serving several loads?
  The question is about the general classification of branch circuits.
Because there is no specific section referenced in the Index by scanning Part II we find the firs section, 210.18, Rating
20 ampere
25 ampere
30 ampere
50 ampere
In Index, find “Branch circuits” under which find “Ratings, 210 – Part II.”
The correct answer is B.
Section 210.18 recognizes standard branch circuit ratings for other than individual branch circuits to be 15, 20, 30, 40, and 50 amperes.
Answer B is not prohibited as a branch circuit rating, however, it is not considered a
“standard branch circuit rating.”

## Slide 77
How many amperes will each phase conductor carry to a 240-volt, 3-phase, 15-kVA heater?
The question is about calculating phase current on a 3-phase circuit.
Use the Ohm’s Law formula:
36.1 amperes
62.5 amperes
72.3 amperes
125 amperes
kVA = 1.73 (3-phase) x E (volts) x I (amps)
15,000 = 1.73 x 240 x I (amps)
I (amps) = 15,000 / (1.73 x 240)
I = 15,000 / 415.2
I = 36.1 amperes
The correct answer is A, 36.1 amperes.

## Slide 78
What is the minimum size Type THW conductor required for a feeder supplying a balanced 100 kVA office lighting load at 3-phase, 480Y/277 volts?
The question is about determining conductor size for a specific load.
2 AWG copper
1 AWG copper
1 AWG aluminum
2/0 AWG aluminum
Calculate the load current.
Use Ohm’[s Law formula
I = P / E x 1.73 [3-phase amps when the load is balanced]
I = 100,000 VA / (480 x 1.73)
I = 120 amperes
The correct answer is A, 36.1 amperes.
Refer to Table 310.15(B)(16) and find that a 1 AWG Type THW copper conductor is rated at 130 amperes, whereas a 2 AWG Type THW copper conductor is only rated for 115 amperes.
Note: Although a 1/0 AWG aluminum conductor is rated at 120 amperes, the question did not specify a conductor material so a copper conductor is chosen (see 110.5)

## Slide 79
A single-phase electric furnace rated at 10 kVA at
240-volts is connected to a single-phase 208-volt
system. What will be the outlet rating of the furnace?
The question is about calculating the output of a 240-volt electric furnace operating
at 208-volts.
5.8 kVA
6.9 kVA
7.2 kVA
7.5 kVA
Using the VA and voltage rating of the furnace determine the resistance of the furnace, with the Ohm’s Law formula:
R = E x E / VA
R = E2 / VA
R = 240 x 240 / 10,000
R = 57,600 / 10,000
R = 5.76 ohms

## Slide 80
A single-phase electric furnace rated at 10 kVA at
240-volts is connected to a single-phase 208-volt
system. What will be the outlet rating of the furnace?
The correct answer is D, 7.5 kVA
5.8 kVA
6.9 kVA
7.2 kVA
7.5 kVA
Using the resistance of the furnace and voltage of the circuit determine the VA at the outlet. Note the definition of outlet in Article 100, Definitions
VA = E x E / R
VA = 208 X 208 / 5.76
VA = 43,264 / 5.76
VA = 7511 Volt-amperes

## Slide 81
What is the current for a 5-horsepower, 230-volt,
3-phase motor with efficiency of 80% and operating at 80% power factor?
The correct answer is B, 14.6 amperes
14.2 amperes
14.6 amperes
16.1 amperes
17.0 amperes
Apply the basic formula for horsepower for a 3-phase load:
HP(horsepower) = E (volts) x I (amps) x 1.73 x efficiency x PF / 746 watts (one horsepower)
or
I (amps) =HP x 746 / (E x 1.73 x efficiency x PF)
I =(5 x 746) / (230 x 1.73 x .80 x .80)
= 3730 / 254.65
I = 14.6 amperes
The question is about determining the current of a motor including efficiency and power
factor.

## Slide 82
What is the minimum size electrical metallic tubing
required for six 3 AWG Type THWN, three 8 AWG THW,
and two 10 AWG THW conductors?
Metric designator 35 (Trade Size 1 ¼)
Metric designator 53 (Trade Size 2)
Metric designator 41 (Trade Size 1 ½)
Metric designator 63 (Trade Size 2 ½)
In the Index, find “Electrical metallic tubing (Type EMT)” under which find “Number of
conductors in, 358.22.”
The question is about calculating the required minimum size of EMT.
Section 358.22 refers to Table 1, Chapter 9 under which Note 6 for combinations of
conductors refers to using the actual dimensions of the conductors or Tables 5 and 5A and
Table 4 for applicable size of tubing. Since the actual dimensions of the conductors were not provided in the question, Tables 5 and 5A will be used.

## Slide 83
What is the minimum size electrical metallic tubing
required for six 3 AWG Type THWN, three 8 AWG THW,
and two 10 AWG THW conductors?
Metric designator 35 (Trade Size 1 ¼)
Metric designator 53 (Trade Size 2)
Metric designator 41 (Trade Size 1 ½)
Metric designator 63 (Trade Size 2 ½)
Refer to Table 4, “Article 358 – Electrical Metallic Tubing (EMT)” under which find the “ Over 2 Wires 40%” column:
41 metric designator ( 1 ½ in.) tubing = 0.814 sq. in.
Referring to Table 5 for conductor areas
3 AWG THWN = 0.0973 sq. in. x 6 = 0.5838 sq. in.
8 AWG THW = 0.0437 sq. in. x 3 = 0.1311 sq. in.
10 AWG THW = 0.0243 sq. in. x 2 = 0.0486 sq. in.
Total conductor area = 0.7635 sq. in.
The correct answer is C, Metric designator 41 (Trade Size 1 ½)

## Slide 84
In areas designated as general care pediatric locations
in a hospital, which statement concerning the
receptacles is TRUE?
Only 15- and 20-ampere receptacles are required to be listed tamper-resistant or shall employ a listed tamper-resistant cover.
All receptacles, regardless of their rating, are required to be listed tamper-resistant or employ a listed tamper-resistant cover.
Tamper-resistant receptacles or tamper-resistant covers are not required.
All receptacles, regardless of their rating, are required to be tamper-proof or employ listed tamper-proof covers.
The question is about receptacles in pediatric locations of a health-care facility.
In Index, find “Receptacles…” under which find “Health care facilities, 517.13, 517.18, 517.19..”
Scan The referenced sections and find “517.18(C), Pediatric Locations,” which requires
receptacles located within the patient care areas of pediatric locations to be listed
tamper-resistant or employ a listed tamper-resistant cover
The correct answer is B.

## Slide 85
Illumination of paint spray booths through glass panels is permitted provided all of the following are complied with EXCEPT:
Portable lighting units are permitted to provide illumination in areas that are readily illuminated with fixed lighting within the spraying area.
The luminaire is installed as described in 516.6(C)(1).
The glass panel installed to separate the luminaire from the spray area must be of heat-treated glass, laminated glass, wired glass, or hammered-wired glass.
The glass panel installed must be sealed to confine vapors, mists, residues, dusts and deposits to the spray area.
The question is about illumination of a paint spray booth.
In Index, find “Spray, application, dipping, and coating processes” under which find “Equipment, 516.5(A)(3), 516.6, 516.7, 516.10, 516.38(B).”
The correct answer is A.
Scan Article 516.6 and find “516.6(D), Portable Equipment,” which does not permit portable
lighting to be used in spraying areas, unless by Exception No. 1 the area is not readily
illuminated by fixed lighting. Answer A is not correct as it state the area is readily illuminated
by fixed lighting in the spraying area.
Section 516.6(C) further confirms that the remaining conditions in answers B, C, and D stated above are met.

## Slide 86
A transformer has a 480-volt, 2-wire primary and a
120-volt, 2-wire secondary and will provide 20 amperes at 120 volts. When the secondary current is 20 amperes, how many amperes of current flow in the primary?
5 amperes
10 amperes
20 amperes
40 amperes
Using the basic transformer formula:
I (primary) = E (secondary) x I (secondary) / E (primary)
I = 120 volts x 20 amps / 480 volts
I = 5 amperes
The question is about calculating transformer currents.
The correct answer is A, 5 amperes

## Slide 87
An industrial heating unit is operated from a 3-phase,
240-volt system. The loads are connected in a delta
configuration and balanced to provide an equal load on each phase. If the total load is 30 kVA, what is the current in the
conductors supplying the unit?
24 amperes
42 amperes
72 amperes
125 amperes
Using the basic Ohm’s Law formula:
  VA = 1.73 x E (volts) x I (amps)
  I (amps) = VA / 1.73 x E
  I = 30 x 1000 VA / (1.73 x 240) volts
  I =30,000 / 415.2
  I = 72.25 amperes
The question is about calculating current to a 3-phase load.

## Slide 88
An industrial heating unit is operated from a 3-phase,
240-volt system. The loads are connected in a delta
configuration and balanced to provide an equal load on each phase. If the total load is 30 kVA, what is the current in the
conductors supplying the unit?
24 amperes
42 amperes
72 amperes
125 amperes
OR
  I = P/E x 1.73 (for 3-phase amps)
  I = 30 x 1000 VA / (240 x 1.73)
  I =30,000 / 415.2
  I = 72.25 amperes
The correct answer is C, 72 amperes

## Slide 89
What is the minimum size Type THW copper conductor
permitted to supply an AC transformer arc welder with a
60 % duty cycle and rated at 43 amperes primary current?
The AC transformer welder connection terminals have a
temperature rating of 600C.
10 AWG
8 AWG
6 AWG
4 AWG
In the Index, find “Conductors” under which find “Welders, electric”, under which find
“Ampacity of supply, 630.11, 630.31.” Section 630.11 is applicable because an arc welder is
specified in the question.
The question is about the minimum size Type THW copper conductor permitted to serve an AC transformer welder.
Section 630.11(A), Individual Welders, requires the ampacity of the supply conductors to be not less than current values determined by multiplying welder nameplate primary rating and the duty cycle factor.
43 amps x .78 (multiplier for 60 percent duty cycle) = 33.54 amperes.

## Slide 90
What is the minimum size Type THW copper conductor
permitted to supply an AC transformer arc welder with a
60 % duty cycle and rated at 43 amperes primary current?
The AC transformer welder connection terminals have a
temperature rating of 600C.
10 AWG
8 AWG
6 AWG
4 AWG
Section 110.14(C) states that conductor shall be selected and coordinated so as not to
exceed the lowest temperature rating of any connected termination. Therefore, even though Type THW is rated for 75oC [see Table 310.15(B)(16)], the 60oC column must be used because of the lower temperature rating of the terminals of the welder. Section 110.40 is not
applicable as it is intended for use on systems rated over 600 volts, nominal.
In Index, find “Connections” under which find “Temperature limitations, 110.14(C), 110.40.”
In Index, find “Ampacities” under which find “Conductors, 310.15, Tables 310.15(B)(16)
through 310.15(B)(21).”
In Table 310.15(B)(16), read down the 60oC column (copper) to next ampacity higher than
33.54 amperes and read left to the AWG column, which requires a 8 AWG Type THW copper conductor. .
The correct answer is B, 8 AWG

## Slide 91
What is the minimum volume required for a junction box containing three 12 AWG and three 10 AWG conductors?
172 cm3 (10.50 cu.in.)
205 cm3 (12.50 cu.in.)
234 cm3 (14.25 cu.in.)
238 cm3 (14.50 cu.in.)
In Index find “Boxes” under which find “Conductors, number in box, 314.16.”
The question is about the minimum “cubic inch box volume” required for a specified number of conductors of different sizes.
Section 314.16 requires the volume of the box to be not less than the fill calculation based on Section 314.16(B), which requires volumes to be added together [as calculated by 314.16(A).
Section 314.16(B)(1), Conductor Fill, requires the fill to be computed using Table 314.16(B).

## Slide 92
What is the minimum volume required for a junction box containing three 12 AWG and three 10 AWG conductors?
172 cm3 (10.50 cu.in.)
205 cm3 (12.50 cu.in.)
234 cm3 (14.25 cu.in.)
238 cm3 (14.50 cu.in.)
The correct answer is C, 234 cm3 (14.25 cu.in.)
Table 314.16(B) requires 36.9 cm3 (2.25 cu.in.) for every 12 AWG and 41.0 cm3 (2.5 cu.in.) for every 10 AWG conductor in the box.
3 x 36.9 cm3 (2.25 cu.in.) = 110.7 cm3 (6.75 cu.in.)
3 x 41.0 cm3 (2.50 cu.in.) = 123 cm3 (7.50 cu.in.)
TOTAL 110.7 cm3 (6.75 cu.in.) + 123 cm3 (7.50 cu.in.) = 234 cm3 (14.25 cu.in.) as the
minimum box volume required.

## Slide 93
Temporary flexible cord wiring is permitted to be laid on floors in an exhibition hall used for display booths, as in trade shows, provided it complies with which one of the following?
Is not over 150 volts between conductors
Is not a branch circuit
Is protected from contact by the general public. GFCI protection does not apply
Is of Type SRD cable
The question is about temporary flexible cord wiring in exhibition halls, which are places of
assembly.
In Index, find “Assembly, places of , 410.10(E), Art. 518” under which none of the subtitles
appear applicable to temporary wiring. You must be familiar with the Code and the scope of
Article 518, located in 518.1 to know that you’re in the correct code article for exhibition halls.
Note that the facility must be designed to accommodate 100 or more occupants at the same
time in order to be considered an assembly occupancy.
The correct answer is C.
Scan Article 518 and find “518.3(B), Temporary Wiring,” which permits flexible cables and
cords approved for hard usage to be laid on floors where protected from contact by the
general public. This section also exempts the GFCI requirements of 590.6. Answer C is correct.

## Slide 94
What is the minimum ampacity required for feeder
conductors supplying two 25-horsepower and one
10-horsepower, 208-volt, 3-phase motors?
(Motors are rated continuous duty)
164 amperes
181 amperes
199 amperes
218 amperes
The question is about minimum ampacity for motor circuit conductors supplying multiple
motors.
In Index, find “Motors” under which find “Conductors” under which find
“Several motors, 430.24”
Section 430.6(A) requires the use of Tables 430.247 through 430.250 when determining the ampacity of conductors for other than for motors built for low speeds (less than 1200 RPM) or high torques, and for multispeed motors.
Section 430.24 requires conductors to have an ampacity equal to the sum of the full-load current rating of all the motors as determined by 430.6(A), plus 25 % of the largest motor.

## Slide 95
What is the minimum ampacity required for feeder
conductors supplying two 25-horsepower and one
10-horsepower, 208-volt, 3-phase motors?
(Motors are rated continuous duty)
164 amperes
181 amperes
199 amperes
218 amperes
Table 430.250 states the following full-load currents under the 208-volt column:
FLC for 25-horsepower motor = 74.8 amps
FLC for 10-horsepower motor = 30.8 amps.
The correct answer is C, 199 amperes
Minimum feeder ampacity:
74.8 x 2 (2-25 HP motors) = 149.6 amperes
30.8 (1-10 HP motor) = 30.8 amperes
18.7 (25% of 74.8) = 18.7 amperes for the “largest” motor of the group
Total = 199.1 amperes

## Slide 96
A Schedule 40 rigid polyvinyl chloride conduit contains
two 500 kcmil Type THW, one 250 kcmil Type THW, and one 1 AWG bare conductors. The minimum permitted
conduit size is:
Metric designator 41 (Trade Size 1 1/2)
Metric designator 53 (Trade Size 2)
Metric designator 63 (Trade Size 2 ½)
Metric designator 78 (Trade Size 3)
The question is about minimum conduit size required for a specified number of conductors
of different sizes.
In Index, find “Conductor fill” under which find “Rigid polyvinyl chloride conduit, 352.22.”
Note: We must find “Area in square inches,” not the diameter for these conductors.
Section 352.22 refers to Table 1, Chapter 9, under which Note 6 for combinations of
conductors refers to using the actual dimensions of the conductors or Table 5 and 5A and
Table 4 for applicable size of conduit. Since the actual dimensions of the conductors were
not provided in the question, Tables 5 and 5A will be used. Where bare conductors are
concerned, Note 8 permits the use of Table 8 for actual dimensions of the conductors.

## Slide 97
A Schedule 40 rigid polyvinyl chloride conduit contains
two 500 kcmil Type THW, one 250 kcmil Type THW, and one 1 AWG bare conductors. The minimum permitted
conduit size is:
Metric designator 41 (Trade Size 1 1/2)
Metric designator 53 (Trade Size 2)
Metric designator 63 (Trade Size 2 ½)
Metric designator 78 (Trade Size 3)
Referring to Table 5 for conductor areas (Table 8 for bare conductors),
(2) 500 kcmil Type THW (Table 5)
= 0.7901 x 2
= 1.5802
    250 kcmil Type THW (Table 5)
            = 0.4596
(1) 1 AWG bare conductor (Table 8)
=0.087
Total conductor area
= 1.5802 + 0.4596 + 0.087
= 2.1268 sq. in.

## Slide 98
A Schedule 40 rigid polyvinyl chloride conduit contains
two 500 kcmil Type THW, one 250 kcmil Type THW, and one 1 AWG bare conductors. The minimum permitted
conduit size is:
Metric designator 41 (Trade Size 1 1/2)
Metric designator 53 (Trade Size 2)
Metric designator 63 (Trade Size 2 ½)
Metric designator 78 (Trade Size 3)
Referring to Table 4 Rigid PVC Conduit (PVC), Schedule 40, and HDPE Conduit, under the “Over 2 Wires 40%” column:
63 metric designator (Trade Size 2 ½) conduit
= 1.878 sq. in.
78 metric designator (Trade Size 3) conduit
= 2.907 sq. in.
The correct answer is D, Metric designator 78 (Trade Size 3)

## Slide 99
The minimum conductor ampacity for a 460-volt, 3-phase
feeder supplying one 10-horsepower squirrel-cage induction motor, one 20-horsepower wound-rotor induction motor, and one 30-horsepower wound-rotor induction motor is:
81 amperes
91 amperes
101 amperes
177 amperes
The question is about feeder conductor ampacity for several motors.
In Index, find “Motors” under which find “Conductors” under which find “Several motors,
430.24.” There is no specific reference under “Motors” to feeder conductors.
Section 430.24 requires conductors to have an ampacity equal to the sum of the full-load
current of all the motors as determined by 430.6(A), plus 25% of the largest motor.
Section 430.6(A) requires the use of Tables 430.247 through 430.250 when determining the
ampacity of conductors for other than for motors built for low speeds (less than 1200 RPM) or high torques, and for multispeed motors.

## Slide 100
The minimum conductor ampacity for a 460-volt, 3-phase
feeder supplying one 10-horsepower squirrel-cage induction motor, one 20-horsepower wound-rotor induction motor, and one 30-horsepower wound-rotor induction motor is:
81 amperes
91 amperes
101 amperes
177 amperes
Table 430.250 lists the applicable full-load currents for 3-phase motors. Perform calculation
as follows:
  FLC for 10-hp squirrel-cage motor = 14 amperes
  FLC for 20-hp wound-rotor motor = 27 amperes
  FLC for 30-hp wound-rotor motor = 40 amperes
  25% of 30-hp FLC (430.24) = 10 amperes .
  Minimum feeder ampacity = 91 amperes
The correct answer is B, 91 amperes

## Slide 101
Class II, Division 2 location may exist due to the
presence of which one of the following conditions?
Accumulated combustible dust sufficient to interfere with normal operation of electric equipment is found
Combustible dust normally in suspension in sufficient quantities to be hazardous and cause an explosion are found
Combustible dust normally sufficient to produce an ignitable mixture is found
In which combustible dust due to abnormal operations may be present in the air in quantities sufficient to produce explosive or ignitable mixtures
The question pertains to classification of hazardous atmospheres in a Class II location.
Section 500.5(C)(2), Class II, Division 2, refers to locations that may be designated as
Class II, Division 2 locations.
In Index, find “Hazardous atmospheres” under which find “Class II locations, 500.5(C).”
The locations described above in conditions A, B, and C would normally fit the Class II,
Division 1 description found in 500.5(C)(1) subdivisions (1), (2), and (3), while the condition
noted in answer D meets the requirements in 500.5(C)(2)(1).
The correct answer is D.

## Slide 102
A commercial building has a continuous lighting load of 33,000 volt-amperes at 240-volts. What are the
minimum size Type THW copper feeder conductors
permitted to serve the load?
1/0 AWG
2/0 AWG
4/0 AWG
250 kcmil
The question is about feeder conductor size.
In Index, find “Feeders” under which find “Calculation of loads, see Loads.” Under “Loads” in Index, find “Feeders, calculations for,” 215.2(A), Article 220, Annex D
Section 215.2(A) requires feeder conductors to have sufficient ampacity to supply the load served, in this case 137.5 amps.
Use the Ohm’s Law formula:
I = VA / E
I = 33,000 / 240 volts
I = 137.5 amperes

## Slide 103
A commercial building has a continuous lighting load of 33,000 volt-amperes at 240-volts. What are the
minimum size Type THW copper feeder conductors
permitted to serve the load?
1/0 AWG
2/0 AWG
4/0 AWG
250 kcmil
Section 215.2(A)(1)(a) requires that where the feeder supplies continuous loads, the
overcurrent device shall not be less than 125% of a continuous feeder load and the minimum feeder conductor shall have an ampacity equal to or greater than 125% of the continuous
load, or in this case, 125% x 137.5 = 172 amps.
In Index, find “Conductors” under which find “Ampacities of, 310.15, Tables 310.15(B)(16)
through 310.15(B)(21)….” Table 310.15(B)(16) provides that a 2/0 AWG Type THW has an
ampacity of 175 amperes.

## Slide 104
A commercial building has a continuous lighting load of 33,000 volt-amperes at 240-volts. What are the
minimum size Type THW copper feeder conductors
permitted to serve the load?
1/0 AWG
2/0 AWG
4/0 AWG
250 kcmil
Note: Section 240.4 requires conductors to be protected in accordance with their ampacity. A 175-ampere overcurrent protective device protects the 2/0 AWG conductor and also
complies with the 125% requirement of Section 215.2(A)(1)(a).
Section 215.2(A) requires feeder conductors to have sufficient ampacity to supply the load
served, in this case 137.5 amps.
The correct answer is B, 2/0 AWG

## Slide 105
What demand factor is permitted to be used for feeder
load calculations for the first 20,000 volt-amperes of a
hotel lighting load?
50 %
60 %
80 %
100 %
The question is about feeder conductor demand factors for a hotel.
Section 215.2(A) refers to Parts III, IV and V of Article 220.
Scan Table 220.42; the “Hotels and motels…” column permits the first 20,000 volt-amperes to have a 50% demand factor.
In Index, find “Feeders” under which find “Calculation of loads, see Loads.” Under “Loads” in
Index, find “Feeders, calculations for,” 215.2(A), Article 220, Annex D.”
Scan Article 220, Part II, and find “220.42, General Lighting,” which refers to Table 220.42 for demand factors for that portion of the total branch-circuit load computed for general
lighting.
The correct answer is A, 50%

## Slide 106
A Class I location shall include locations containing all of the following atmospheres EXCEPT:
Hydrogen
Ammonia
Propane
Oxygen
The question pertains to classification of hazardous atmospheres in a Class I location.
Scan Section 500.6(A)(2) and (4), in the Informational Notes, and find “Class I Group
Classification” under which find all of the atmospheres are listed except oxygen.
Note: Gasoline is also a Class I Group D flammable liquid.
In Index, find “Hazardous atmospheres” under which find “Class I locations, 500.5(B)” and
“Groups A through G, 500.6”
The correct answer is D.

## Slide 107
What is the minimum required horsepower rating of a
disconnecting means serving a machine consisting of one
10-horsepower, one 20-horsepower motor, all of the
squirrel-cage type rated at 3-phase, 460-volt? (assume
Design B motors)
50 horsepower
60 horsepower
75 horsepower
100 horsepower
The question is about rating of a disconnecting means for multiple motors used together.
Scan Article 430, Part IX and find “430.110, Ampere Rating and Interrupting Capacity.”
In Index, under “Motors” under which find “Disconnecting means, 430.75, 430.95,
430-Part IX…”
Section 430.110(C), covering combination loads, notes where two or more motors are used together the ampere and horsepower ratings of the disconnecting means must be
determined by 430.110(C)(1) – (3). This will be a multi-step process as in our case the
disconnecting means would have to satisfy both the horsepower rating requirements and
ampere rating requirements. The compbined full-load currents and locked-rotor currents
will be considered as a single motor.

## Slide 108
What is the minimum required horsepower rating of a
disconnecting means serving a machine consisting of one
10-horsepower, one 20-horsepower motor, all of the
squirrel-cage type rated at 3-phase, 460-volt? (assume
Design B motors)
50 horsepower
60 horsepower
75 horsepower
100 horsepower
To satisfy the full-load current requirements the second paragraph of 430.110(C)(1) provides that the full-load current equivalent to the horsepower rating of each motor shall be selected from Tables 430.247, 430.248, 430.249, or 430.250, and added to obtain an equivalent
full-load current for the combined load.
For 3-phase motors, use Table 430.250 under the heading “Induction Type, Squirrel Cage
and Wound Rotor (Amperes)”:
10-horsepower = 14 FLA
20-horsepower = 27 FLA
30-horsepower = 40 FLA .
Total = 81 FLA

## Slide 109
What is the minimum required horsepower rating of a
disconnecting means serving a machine consisting of one
10-horsepower, one 20-horsepower motor, all of the
squirrel-cage type rated at 3-phase, 460-volt? (assume
Design B motors)
50 horsepower
60 horsepower
75 horsepower
100 horsepower
Section 430.110(C)(2) requires the disconnecting means to have an ampere rating of at least 115% of the full-load current condition from 430.110(C)(1) [115% x 81 = 93 amperes]. Since
there is no motor shown in Table 430.250 that has a FLA of 93, go to the next higher FLA,
which is the same as though there was (1) 75-horsepower motor (96-amps).
Next, according to the third paragraph of 430.110(C)(1), use the same method using the
locked-rotor current selected from Table 430.251(B) (assume Design B motors). The values
selected for the three motors are 81, 145, and 218 locked-rotor currents, which added
together = 444 amperes. In Table 430.251(B), using the equivalent value for a single motor
find the locked-rotor current for a 75-horsepower motor is 543 amperes. A 60 hp motor is
only rated at 435 amperes so the 75 hp rating is used.
The correct answer is C, 75 horsepower

## Slide 110
Which of the following is the NEC recommended
maximum voltage drop on a feeder and branch circuit
to the farthest outlet?
1.5 percent
2 percent
3 percent
5 percent
The question is about the recommended maximum voltage drop on a circuit consisting of a
feeder and brand circuit.
Section 210.19(A) Informational Note No. 4, states a drop of 3 percent for branch circuits and 5 percent for feeders and branch circuits is recommended with this measurement being
taken at the farthest outlet.
In Index, find “Voltage and volts” under which find “Drop” under which find “Branch circuits,
210.19(A) Informational Note No. 4”
The correct answer is D, 5 percent
Note: As it turns out there is no direct reference to voltage drop on feeders in the
NEC, however, the same information can be found in 215.2(A)(3) Informational Note 2.

## Slide 111
What is the total calculated load of an installation of
12 m (40 ft.) of a fixed multioutlet assembly, installed in a continuous length in office occupancy?
12 amperes
16 amperes
20 amperes
30 amperes
The question is about calculated load for multioutlet assemblies.
Section 220.14(H)(1) provides that each 1.5 m (5 ft.) or fraction thereof of each separate and continuous length shall be considered as one outlet of not less than 180 VA capacity.
In Index, find “Multioutlet assembly” under which find “Calculation of load, 220.14(H).”
The correct answer is A, 12 amperes
Proceed with the calculations.
12 m (40 ft.) / 1.5 m (5 ft.) = 2.5 m (8 ft.)
2.5 m (8 ft.) x 180 VA = 1440 VA
1440 VA / 120 volts = 12 amperes

## Slide 112
A 3-phase, 4-wire, 480Y/277 feeder has all loads connected
line to neutral. What is the current in the neutral conductor?
(Phase A = 30 Amp load)
(Phase B = 40 Amp load)
(Phase C = 50 Amp load)
10 amperes
20 amperes
17.3 amperes
24.6 amperes
The question is about neutral current in an unbalanced 3-phase circuit.
Answer Formula
√ I2A + I2B + I2C – (IAIB) – (IBIC) – (ICIA)
√ 302 + 402 + 502 - (30 x 40) – (40 x 50) – (50 x 30)
√ 900 + 1600 + 2500 – 1200 – 2000 – 1500
√ 5000 – 4700
√ 300 =17.3 amperes ( The square root of 300 is 17.3.)
The correct answer is C, 17.3 amperes

## Slide 113
Without considering any specific type of load, which of
the following would be the correct ampacity per
conductor for Twelve Type THHN 12 AWG copper
current-carrying conductors installed in a single raceway?
15 amperes
20 amperes
21 amperes
30 amperes
The question is about the ampacity of multiple current-carrying conductors in a single
raceway.
Section 310.15(A)(1) permits ampacities of conductors to be determined by 310.15(B) or by engineering supervision. The use of 310.15(B) (NEC Tables) is the most common practice
and, in our case, there is not enough information provided in the question for additional
calculations.
In Index, find “Ampacities” under which find “Conductors, 310.15, Tables 310.15(B)(16) through 310.15(B)(21).”
Table 310.15(B)(16) gives the ampacity of a 12 AWG Type THHN conductor in a raceway as 30 amperes when not more than three current-carrying conductors are installed and the ambient temperature does not exceed 32o C (86o F).

## Slide 114
Without considering any specific type of load, which of
the following would be the correct ampacity per
conductor for Twelve Type THHN 12 AWG copper
current-carrying conductors installed in a single raceway?
15 amperes
20 amperes
21 amperes
30 amperes
Because the question involves more than three conductors, review 310.15(B)(3) which gives
reference to the ampacity adjustment factors in Table 310.15(B)(3)(a).
30 amps x 50% = 15 amperes.
Table 310.15(B)(3)(a) requires a 50 percent, reduction of the 30-ampere value for (12)
conductors in a conduit.
The correct answer is A, 15 amperes.
Note: The definition of ampacity in Article 100 provides that “the conditions of use”
determine the computed ampacity.

## Slide 115
Which one of the following statements concerning
agricultural buildings that contain excessive dust and
dust with water is NOT true?
Switches and controllers shall utilize weatherproof enclosures or boxes shall be designed to minimize the entrance of dust and shall have no openings (such as holes for attachment screws) through which dust could enter the enclosure.
A luminaire in a location exposed to building cleansing water shall be “listed as suitable for use in wet locations.”
Liquidtight flexible nonmetallic conduit is permitted for a wiring method.
Type NM cable may be used for wiring in these areas.
The question is about equipment and wiring methods in agricultural buildings.
Section 547.6 refers to Section 547.5(C) for switches and controllers’ enclosures requirements.
In Index, find “Agricultural buildings” under which find “Luminaires, 547.8,””Switches…547.6,”
and “Wiring methods, 547.5.”
Section 547.5(A) identifies liquidtight flexible nonmetallic conduit as an acceptable wiring method but does not include Type NM cable. Answer C is true. Answer D is not true.

## Slide 116
Which one of the following statements concerning
agricultural buildings that contain excessive dust and
dust with water is NOT true?
Switches and controllers shall utilize weatherproof enclosures or boxes shall be designed to minimize the entrance of dust and shall have no openings (such as holes for attachment screws) through which dust could enter the enclosure.
A luminaire in a location exposed to building cleansing water shall be “listed as suitable for use in wet locations.”
Liquidtight flexible nonmetallic conduit is permitted for a wiring method.
Type NM cable may be used for wiring in these areas.
Section 547.8(C) requires luminaires in locations exposed to building cleansing water to be
listed as suitable for use in wet locations. Answer B is true.
Section 547.5(C)(1) and (2) requires enclosures that limit the entrance of dust, and
weatherproof enclosures for switches and controllers in excessive dust and wet locations.
Answer A is true.
The correct answer is D.

## Slide 117
Branch-circuit conductors supplying two 4 kVA
wall-mounted ovens and one 5 kVA counter-mounted
cooking unit in the same dwelling unit kitchen shall
have a minimum ampacity of:
30 amperes
35 amperes
40 amperes
50 amperes
The question is about branch-circuit calculations for cooking equipment.
Section 220.55, Electric Ranges and Other Cooking Appliances – Dwelling Unit(s), provides that cooking appliances rated in excess of 1 ¾ kW shall be permitted to be computed in accordance with Table 220.55. This table requires column C to be used, except as otherwise permitted in Note 3. Note 3 permits cooking units, etc., having a nameplate rating greater than 1 ¾ kW through 8 ¾ kW to be added together. The sum will then be multiplied by the demand factor specified in Column A or B for the given number of appliances.
In Index, find “Branch circuits” under which find “Calculation of loads, 220 – Part II, Annex D;”
or, find “Loads” under which find “Appliances, household cooking, demand table, 220.55.”

## Slide 118
Branch-circuit conductors supplying two 4 kVA
wall-mounted ovens and one 5 kVA counter-mounted
cooking unit in the same dwelling unit kitchen shall
have a minimum ampacity of:
30 amperes
35 amperes
40 amperes
50 amperes
The question, however, addresses a branch-circuit load with a specific combination of cooking appliances addressed in Note 4. Note 4 requires the branch-circuit load for a counter-mounted cooking unit and not more than two wall-mounted ovens supplied from a single branch circuit and located in the same room to be calculated by adding the nameplate rating of the
individual appliances and treating the total as equivalent to one range. Note 1 provides that
each kW exceeding 12 is to be increased 5 % of column C.
= 4000 W + 4000 W + 5000 W
= 13,000 W

## Slide 119
Branch-circuit conductors supplying two 4 kVA
wall-mounted ovens and one 5 kVA counter-mounted
cooking unit in the same dwelling unit kitchen shall
have a minimum ampacity of:
30 amperes
35 amperes
40 amperes
50 amperes
Because the rating of the three ranges are now combined into “one” range which is over
12 kW, Note 2 and Column C of Table 220.55 are applicable.
= 13 kW – 12 kW = 1 x ( 5% of 8 kW)
= 0.4 kW
= 8 kW + 0.4 kW
= 8.4 kW (kVA)
Assuming 240-volt ranges, the minimum branch-circuit conductor ampacity :
= 8.4 kW x 1000 / 240
= 35 amperes (Ohm’s Law formula I = P / E)
The correct answer is B, 35 amperes.

## Slide 120
Determine the voltage a percolator would receive if the neutral conductor were broken on a muliwire circuit
with a 720-watt percolator on Phase A and a
1200-watt fry pan on Phase B.
120 volts
150 volts
240 volts
720 volts
The question is about voltages on muliwire circuits when the neutral is opened.
Find the resistance of each load.
Use Ohm’s Law formula R = E2 / P (P = Power in VA)
RA (720 volt-amperes)
= E2 / VAA
= 1202 / 720
= 14400 / 720
= 20 ohms

## Slide 121
Determine the voltage a percolator would receive if the neutral conductor were broken on a muliwire circuit
with a 720-watt percolator on Phase A and a
1200-watt fry pan on Phase B.
120 volts
150 volts
240 volts
720 volts
RB (1200 volt-amperes)
= E2 / VAB
= 1202 / 1200
= 14400 / 1200
= 12 ohms
Find total circuit resistance:
R Total = 20 ohms + 12 ohms
R Total = 32 ohms

## Slide 122
Determine the voltage a percolator would receive if the neutral conductor were broken on a muliwire circuit
with a 720-watt percolator on Phase A and a
1200-watt fry pan on Phase B.
120 volts
150 volts
240 volts
720 volts
Find the total series circuit current:
I = E / R
I = 240 / 32
I = 7.51 amps
Find the voltage across percolator load.
E = I x R
E = 7.51 x 20
E = 150.2 volts
The correct answer is B, 150 volts

## Slide 123
Under normal conditions, the classification of an
unventilated pit or depression below the floor level of a commercial garage where oil changes are performed on gasoline-powered vehicles is classified as:
Class I, Division 1
Class I, Division 2
Class I, Zone 1
Class II, Zone 2
The question is about classification of locations in commercial garages.
Note: Because oil changes are performed in the garage [fluid changes (e.g., oil, anti-freeze,
transmission fluid, brake fluid, air-conditioning refrigerants], you must first look at the
definitions in overhauls, painting or repairs that involve draining the fuel tanks, 511.2 defines the location as a minor repair garage.
In Index, find “commercial garages,” which refers you to Garages, commercial,” under which
find “Classification of locations, 511.3,” which lists parking garages, repair garages with
dispensing, major repair garages, and minor repair garages. You must carefully read the
question to find the needed clues to direct you to the correct type of garage in order to find
the correct answer.

## Slide 124
Under normal conditions, the classification of an
unventilated pit or depression below the floor level of a commercial garage where oil changes are performed on gasoline-powered vehicles is classified as:
Class I, Division 1
Class I, Division 2
Class I, Zone 1
Class II, Zone 2
Next, we have to determine if the vehicle is using a heavier-than-air fuel such as gasoline
(a class 1 liquid) or LPG (a gaseous fuel) or is it using a lighter-than-air fuel such as hydrogen or natural gas. Section 511.3(C), Repair Garages, Major and Minor, specify the use of
Table 511.3(C)(3) for vehicles using Class 1 liquids or heavier-than-air fuels.
The correct Answer is B.
Next, find Table 511.3(C) which states that in a minor repair garage without dispensing or
transfer of Class 1 liquids or gaseous fuels the entire space within any pit, below-grade work
area, or sub-floor work area that is not ventilated is to be classified as a Class I, Division 2.

## Slide 125
A. Is never
Chapter 8 covers all communication systems and _____subject to requirements of chapter 1-7
B. Is always
C. May be – if specifically referenced
Your answer would be C. May be – if specifically
referenced
What code reference are we going to use?
D. None of the above
90.3

## Slide 126
A. Shall
Internal wiring of communication equipment ____be inspected by the AHJ
B. Shall not
C. If modified in the field shall
Your answer would be D. If approved by a NRTL,
need not
What code reference are we going to use?
D. If approved by a NRTL, need not
90.7

## Slide 127
A. Set with torque rated tools
Electrical screw terminal connections are to be ____unless otherwise allowed.
B. Hand tightened
C. Wrench tight
Your answer would be A. Set with torque rated tools
What code reference are we going to use?
D. Set with a tensioned driver
110.14(D)

## Slide 128
A. In the NEC
The standard for Neat and Workman Like installations is?
B. In the NFPA standards
C. In the practical wiring handbook
Your answer would be D. Based on the AHJ standards
What code reference are we going to use?
D. Based on the AHJ standards
110.12

## Slide 129
A. Listed if more than one conductor
Conductor terminations shall be for ?
B. Aluminum – if listed
C. Designed to not damage the conductor
Your answer would be D. All of the above
What code reference are we going to use?
D. All of the above
110.14(A)

## Slide 130
A. Copper
Conductors used for electrical wiring are to be made of ____if not otherwise specified.
B. Tin plated copper
C. Silver plated copper
Your answer would be A. Copper
What code reference are we going to use?
D. Copper covered aluminum
110.5

## Slide 131
A. A round wire that is .001 inches in diameter.
A circular mil is?
B. A wire that has a circumference of 1 inch
C. The Cross section of a wire that is .1 square inches
Your answer would be A. A round wire that is .001 inches in diameter
What code reference are we going to use?
D. The inverse of a square mil area of the square wire
It is not code but Chapter 9 Table 8

## Slide 132
A. Is not used for Ethernet compared to
Cat 5 cable ___5e cable.
B. Is designed for longer runs than
C. Can only handle gigabit speeds compared to
Your answer would be D. Is the basic cable compared to
What code reference are we going to use?
D. Is the basic cable compared to
Industry specification

## Slide 133
A. Plenum rated low voltage cable
PLFA cable is ____as defined in
NEC 760.
B. Power Limited Fire Alarm cable
C. Preferred Line voltage Fire assembly cable
Your answer would be B. Power Limited Fire Alarm Cable
What code reference are we going to use?
D. Pressurized Line – Frequency adjusted cable
760, Part III

## Slide 134
  6“
  12“
  18“
  24”
Section 300.5(A) references Table 300.5, which in Column 4 allows a 20-amp, 120 volt residential branch circuit with GFCI protection to be buried a minimum of 12”.
So the answer would be B.
In Index, find “Underground wiring.” under which find “Minimum cover requirements, 300.5(A).”
The question is about minimum cover requirements for underground cable.
What is the minimum cover requirement for 12 AWG Type UF cable
used for an underground residential branch circuit rated 120 volts and connected to a GFCI circuit breaker?

## Slide 135: Under general conditions conductors installed in raceways shall be stranded if larger than what size?
  12 AWG
  10 AWG
  8 AWG
  6 AWG
Section 310.106(C) provides that when installed in raceways, conductors of size 8 AWG and larger shall be stranded.
So the answer would be B. Did you read the Question?
In Index, find “Conductors.” under which find “Stranded, 310.106(C).”
The question is about stranded conductors installed in raceways.

## Slide 136: What is the minimum size copper equipment grounding conductor required for grounding a water heater connected to a circuit protected by a 40-amp overcurrent device?
  14 AWG
  12 AWG
  10 AWG
  8 AWG
Section 250.122 refers to Table 250.122, which shows a minimum 10 AWG copper equipment grounding conductor for overcurrent devices rated more than 20 amperes and not more than 60 amperes.
So the answer would be C.
In Index, find “Equipment grounding conductors,” under which find “Sizing, 250.122, 250.190(C)(3).”
The question is about the sizing of equipment grounding conductors.

## Slide 137
A wireway contains unspliced conductors with a total cross sectional area of 16.00 sq. in. What is the minimum allowable size of this wireway?
A. 6X6
B. 8X8
C. 9X9
Your answer would be C. 9X9
What code reference are we going to use?
D. 4X4
Calculations: 16.00 sq. in. X 5 = 80 sq. in.
square root of 80 = 8.94 or 9
376.22

## Slide 138
A. Grounded conductor
For three and four way switches, the wiring of these switches must be done so that the switching is done in which conductor?
B. Ungrounded conductor
C. Grounding conductor
Your answer would be B. Ungrounded conductor
What code reference are we going to use?
D. Grounded or Ungrounded conductor
404.2(A)

## Slide 139
Ground
A ground –fault current path is an electrically conductive path from the point of a ground fault through normally noncurrent carrying conductors, equipment, or the earth to the _______.
B. Earth
C. Electrical supply source
Your answer would be C.
What code reference are we going to use?
D. None of these
100

## Slide 140
A. A four story commercial building
NM shall be permitted to be used as a wiring method in which of the following installations?
B. Embedded in poured concrete
C. Service entrance conductors in dwellings
Your answer would be A. A four story commercial building
What code reference are we going to use?
D. Concealed work in damp or corrosive locations
334.10

## Slide 141
A. 12
For straight pulls, the length of a pull box shall not be less than ______times the outside diameter,
over the sheath, of the largest shielded or
lead-covered conductor or cable entering the box on systems over 1,000V.
B. 16
C. 24
Your answer would be D.
What code reference are we going to use?
D. 48
314.71(A)

## Slide 142
A. the authority having jurisdiction
Type ITC cable shall be installed in
industrial establishments where the conditions of maintenance and supervision ensure that
only ____will service the installation.
B. Authorized persons
C. General public
Your answer would be D.
What code reference are we going to use?
D. Qualified persons
727.4

## Slide 143
A. 1
Except by special permission, no conductor larger than ___AWG shall be installed in a cellular metal floor raceway.
B. 1/0
C. 4/0
Your answer would be B.
What code reference are we going to use?
D. None of these
374.20

## Slide 144
A. Six inches
A 120 volt, residential branch-circuit, is rated at 20 A and is installed underground. The UF cable, which has GFCI protection, is required to be
buried a minimum depth of ?
B. Twelve inches
C. Eighteen inches
Your answer would be B. Twelve inches
What code reference are we going to use?
D. Twenty-four inches
Table 300.5

## Slide 145
A. ½ inch
What is the minimum distance allowable that a bored hole shall be from the edge of a wooden member containing conductors?
B. ¾ inch
C. 1 inch
Your answer would be D. 1 ¼ inch
What code reference are we going to use?
D. 1 ¼ inch
300.4(A)(1)

## Slide 146
A. 2 inch
What is the minimum allowable trade size of rigid metal conduit which can contain (3) #6 THW and (1) #8 THW insulated conductor?
B. 1 ½ inch
C. 1 inch
Calculations
What code reference are we going to use?
D. 1 ¼ inch
300.4(A)(1)
Your answer would be 1 inch Trade Size = .355 sq. in.
#6 THW = .0726 X 3 = .2178 sq. in.
#8 THW = .0437 sq. in.
.2615 sq. in.

## Slide 147
A. The total load supplied by the panelboard
A panelboard is not required to have individual overcurrent protection when the panelboard feeder has overcurrent protection not greater than what?
B. The feeder rating
C. The panelboard rating
Your answer would be C. The panelboard rating
What code reference are we going to use?
D. 100 amperes or less
408.36

## Slide 148
A panelboard is protected on the supply side of the panelboard by two main breakers. What is the maximum number of overcurrent devices allowed?
A 40
B. 42
C. 44
Your answer would be B. 42
What code reference are we going to use?
D. 48
408.36 ex. 2

## Slide 149
Three (3) #2 ungrounded conductors installed in rigid nonmetallic conduit enter a junction box. The conductors may be protected by which of the following means?
A 1 only
B. 2 only
C. Either 1 or 2
Your answer would be C. Either 1 or 2
What code reference are we going to use?
D. Neither 1 or 2
300.4(G)
A smoothly rounded identified fitting
Substantial identified insulating material securely fastened in place which separates the conductors from the raceway.

## Slide 150
A. Underground installations
Rigid nonmetallic conduit is permitted to be used for any of the following except?
B. For the support of lighting fixtures when effectively braced
C. Concealed in walls
Your answer would be B. For support of lighting fixures
What code reference are we going to use?
D. In cinder fill
352.10 & 352.12

## Slide 151
A. 20 percent
Underfloor raceways shall have a maximum conductor fill of what percent?
B. 40 percent
C. 60 percent
Your answer would be B. 40 percent
What code reference are we going to use?
D. 100 percent
390.6

## Slide 152
0.40
0.60
0.70
0.80
When the calculated number of conductors or cables, all of the same size, installed in a conduit or in tubing includes a decimal, the next higher whole number shall be used when this decimal is _______or larger.
Your answer would be D.
What code reference are we going to use?
Chapter 9, notes to tables, note 7

## Slide 153
A. Vapors or fumes
Junction boxes installed in underfloor raceways shall be sealed against the entrance of what?
B. Water or concrete
C. Dust or dirt particles
Your answer would be B. Water or concrete
What code reference are we going to use?
D. All of the above
390.13

## Slide 154
A. 3-phase 4-wire delta supplying motor loads
The neutral conductor is considered a current carrying conductor in which of the following circuits?
B. 3-phase 4-wire wye supplying motor loads
C. 3-phase 4-wire delta supplying fluorescent lighting
Your answer would be D. 3-phase 4-wire wye supplying fluorescent lighting
What code reference are we going to use?
D. 3-phase 4-wire wye supplying fluorescent lighting
310.15(B)(5)(c)

## Slide 155
A. Be run in the same raceway
Conductors connected in parallel shall meet all of the following conditions except?
B. Have the same insulation type
C. Be terminated in the same manner
Your answer would be A. Be run in the same raceway
What code reference are we going to use?
D. Have the same circular mil area
310.10(H)(2)

## Slide 156
2 = Phase Constant for Single-Phase
K = Resistivity Factor – Ohms/cmil ft., 12.9 for Cu and 21.2 for Al at 75o C
I = Current in Amps
L = Length in Feet
CM = Circular Mils
VL = Volts Loss = % voltage drop x applied Voltage
Voltage Drop
Wire Size in Circular Mils Single-Phase = 2KIL
VL

## Slide 157
√3 = Phase Constant for Three-Phase (1.732)
K = Resistivity Factor – Ohms/cmil ft., 12.9 for Cu and 21.2 for Al at 75o C
I = Current in Amps
L = Length in Feet
CM = Circular Mils
VL = Volts Loss = % voltage drop x applied Voltage
Voltage Drop
Wire Size in Circular Mils Three-Phase = √3KIL
VL

## Slide 158
Multiply the horsepower by 746 watts.
HORSE POWER
Amps measure electrical current.
Horsepower is the amount of energy a motor creates when in use.
Given horsepower and volts, it is possible to calculate amps.
The calculation of amps uses Ohm's Law, which is amps times volts
equals watts.
For example, an engine at two horsepower with 230 volts would be calculated as two horsepower times 746 watts, which equals 1492. (2 x 746 = 1492)
Divide the number calculated in Step 1 by the amount of volts to calculate watts. In the example, 1492 would be divided by 230, which equals about 6.49 amps. (1492 / 230 = 6.49)

## Slide 159
HORSE POWER
How to convert horsepower to kilowatts
How to convert power in horsepower (hp) units to kilowatts (kW) units.
Mechanic / Hydraulic horsepower to kilowatts
One mechanic or hydraulic horsepower is equal to 0.745699872 kilowatts:
1 hp(I) = 745.699872 W = 0.745699872 kW
So the power conversion of horsepower to kilowatts is given by:
P(kW) = 0.745699872 ⋅ P(hp)
Example
Convert 10 hp to kW:
P(kW) = 0.745699872 ⋅ 10hp = 7.45699872 kW

## Slide 160
HORSE POWER
How to convert horsepower to kilowatts
How to convert power in horsepower (hp) units to kilowatts (kW) units.
Electrical horsepower to kilowatts
One electrical horsepower is equal to 0.746 kilowatts:
1 hp(E) = 746 W = 0.746 kW
So the power conversion of horsepower to kilowatts is given by:
P(kW) = 0.746 ⋅ P(hp)
Example
Convert 10 hp to kW:
P(kW) = 0.746 ⋅ 10hp = 7.460 kW

## Slide 161
The terms “bonding” and “grounding” are often employed interchangeably as general terms in the electrical industry to imply or mean that a specific piece of electrical equipment, structure, or enclosure is somehow referenced to earth.
DIFFERENCES BETWEEN BONDING AND
GROUNDING
In fact, “bonding” and “grounding” have completely different meaning and employ different electrical installation methodologies.

## Slide 162
“Bonding” is a method by which all electrically conductive materials and metallic surfaces of equipment and structures, not normally intended to be energized, are effectively interconnected together via a low impedance conductive means and path in order to avoid any appreciable potential difference between any separate points.
DIFFERENCES BETWEEN BONDING AND
GROUNDING
For example, airplanes do not have any connection to the planet Earth when they are airborne. It is extremely important for the safety and welfare of passengers, crew, and aircraft the all metallic parts and structures of an airplane are effectively bonded together to avoid difference of potential between structures and parts when traveling at high rates of speed or when the frame of the aircraft is struck by lightning.
The bonded interconnections of any specific electrically conductive materials, metallic surfaces of enclosures, electrical equipment, pipes, tubes, or structures via a low impedance path are completely independent and unrelated to any intended contact or connection to the Earth.

## Slide 163
The laboratories and satellites orbiting in space above the planet Earth
obviously have no direct connection with the surface of our planet.
All of the conductive surfaces of these orbiting laboratories and satellites must be effectively bonded together in order to avoid differences of potential from being induced across their surfaces from the countless charged particles and magnetic waves traveling through space.
DIFFERENCES BETWEEN BONDING AND
GROUNDING

## Slide 164
The common mean to effectively bond different metallic surfaces of enclosures, electrical equipment, pipes, tubes or structures together is with a copper conductor, rated lugs, and the appropriate bolts, fasteners, or screws.
DIFFERENCES BETWEEN BONDING AND
GROUNDING
In addition to preventing potential differences that may result in hazards, effectively bonded equipment can also be employed to adequately and safely conduct phase-to-ground fault current, induced currents, surge currents, lightning currents, or transient currents during such abnormal conditions.
Other effectively bonding means between different metallic parts and pieces might employ brackets, clamps, exothermic bonds, or welds to make an effectively connections.

## Slide 165
“Grounding” is a term used rather exclusively in North American to indicate a direct or indirect connection to the planet Earth or to some conducting body that serves in place of the Earth.
The connection(s) to Earth can be intentional or unintentional by an assortment of metallic means intended to be employed as a designated grounding electrode.
A designated grounding electrode is the device that is intended to establish the direct electrical connection to the earth.
A common designated grounding electrode is often a copper clad or copper flashed steel rod.
The designated grounding electrode might be a water pipe, steel columns of a building or structure, concrete encased steel reinforcement rods, buried copper bus, copper tubing, galvanized steel rods, or semi conductive neoprene rubber blankets. Gas pipes and aluminum rods can not be employed as grounding electrode
The grounding electrode conductor is the designed conductor that is employed to connect the grounding electrode(s) to other equipment grounding conductors, grounded conductor, and structure.
DIFFERENCES BETWEEN BONDING AND
GROUNDING

## Slide 166
“Grounding” is a term used rather exclusively in North American to indicate a direct or indirect connection to the planet Earth or to some conducting body that serves in place of the Earth.
The connection(s) to Earth can be intentional or unintentional by an assortment of metallic means intended to be employed as a designated grounding electrode.
A designated grounding electrode is the device that is intended to establish the direct electrical connection to the earth.
A common designated grounding electrode is often a copper clad or copper flashed steel rod.
The designated grounding electrode might be a water pipe, steel columns of a building or structure, concrete encased steel reinforcement rods, buried copper bus, copper tubing, galvanized steel rods, or semi conductive neoprene rubber blankets. Gas pipes and aluminum rods can not be employed as grounding electrode
The grounding electrode conductor is the designed conductor that is employed to connect the grounding electrode(s) to other equipment grounding conductors, grounded conductor, and structure.
DIFFERENCES BETWEEN BONDING AND
GROUNDING

## Slide 167
A. 200%
An ac arc welder shall have overcurrent protection at not more than what percentage of the rated primary current of the welder?
B. 150%
C. 125%
Your answer would be A. 200%
What code reference are we going to use?
D. 100%
630.12(A)

## Slide 168
A. 15 feet
A branch circuit voltage that exceeds 277V to ground and does not exceed 600V between conductors is used to wire the auxiliary equipment of electrical discharge lamps mounted on poles. The minimum height of these luminaries must not be less than?
B. 18 feet
C. 22 feet
Your answer would be C. 22 feet
What code reference are we going to use?
D. 33 feet
210.6(D)(1)(a)

## Slide 169
A. 110 Amps
A department store (continuous load) feeder supplies a lighting load of 103 Amps. The minimum size overcurrent protection device permitted for this feeder is?
B. 125 Amps
C. 150 Amps
Your answer would be C. 150 Amps
What code reference are we going to use?
D. 175 Amps
215.3
103 Amps X 1.25 = 128.75 Amps So you go to the next standard size

## Slide 170
A. 1 foot
An outdoor disconnecting means for a mobile home must be installed so the bottom of the enclosure is not less than how many feet above the finished grade or working platform?
B. 2 feet
C. 3 feet
Your answer would be B. 2 feet
What code reference are we going to use?
D. 6 feet 7 inches
550.32(F)

## Slide 171
A. 0.063 ohms
What is the alternating-current ohms-to-neutral resistance for 1000 feet of 4/0 AWG aluminum conductor in a steel raceway?
B. 0.10 ohms
C. 0.11 ohms
Your answer would be B. 0.10 ohms
What code reference are we going to use?
D. 0.33 ohms
Chapter 9 Table 9

## Slide 172
A. Where conductors enter the box in a raceway that will accept a future grounded conductor.
When installing wiring for switches, in which condition below would a grounded conductor be required to be located at the switch box?
B. Where the box enclosing the switch is accessible for the installation of an additional or replacement cable.
C. When two or more switches are located in the room.
Your answer would be C. When two or more switches…
What code reference are we going to use?
D. Where a switch controls a receptacle load
404.2(C)

## Slide 173
A. 15 seconds
The residual voltage of a capacitor, rated not over 600 volts, must be reduced to 50 volts or less within _____after the capacitor is disconnected from the source of supply.
B. 45 seconds
C. 1 minute
Your answer would be C. 1 minute
What code reference are we going to use?
D. 2 minutes
460.6(A)

## Slide 174
A. Chapter 3 raceways
Communication wires and cables may be installed in properly listed?
B. Riser rated communication raceways
C. Innerduct
Your answer would be D. Any of the above
What code reference are we going to use?
D. Any of the above
800.110

## Slide 175
A. Article 300
The Article that contains the requirements for remote control, signaling and power limited circuits that are not an integral part of a device or appliance is?
B. Article 640
C. Article 725
Your answer would be C. Article 725
What code reference are we going to use?
D. Article 800
725.1

## Slide 176
A. 30 Volt
A class 1 power limited circuit has a maximum voltage rating of?
B. 50 Volts
C. 150 Volts
Your answer would be A. 30 Volts
What code reference are we going to use?
D. 300 Volts
725.41

## Slide 177
A. 24, 500
A class 2 AC circuit is rated for maximum of ____ volts and ____VA?
B. 30, 150
C. 60, 1000
Your answer would be D. 150, 75
What code reference are we going to use?
D. 150, 75
Chapter 9 Table 11(A)

## Slide 178
A. Electric shock
A class 2 circuit is safer than a class 3 circuit from the standpoint of?
B. Fire ignition potential
C. Ability to generate power
Your answer would be A. Electric shock
What code reference are we going to use?
D. Remote control capability
725.2

## Slide 179
A. 100 Volts
The insulation of Class 2 power limited cable is?
B. 150 Volts
C. 300 Volts
Your answer would be B. 150 Volts
What code reference are we going to use?
D. 600 Volts
725.179(G)

## Slide 180
A. Blocked
Openings around electrical penetrations in fire rated walls or floors need to be ____to maintain fire ratings.
B. Fire-stopped
C. Sealed
Your answer would be B. Fire-stopped
What code reference are we going to use?
D. Tested
725.3 – 300.21

## Slide 181
A. Article 80
Which Article covers wiring methods for all wiring installations – unless modified by other articles?
B. Article 725
C. Article 300
Your answer would be C. Article 300
What code reference are we going to use?
D. Article 110
300.1(A)

## Slide 182
A. Class 2 control circuits
The provisions of Article 300 are not intended to apply to?
B. Class 1 electric power circuits
C. Wiring under 120 Volts
Your answer would be D. The conductors that form an integral part of
equipment
What code reference are we going to use?
D. The conductors that form an integral part of equipment
300.1(B)

## Slide 183
A. Are not to be installed unless it is a recognized wiring system
Single conductors_________
B. Can be installed if in a conduit
C. Can never be installed
Your answer would be A. Are not to be installed unless it is a recognized wiring system
What code reference are we going to use?
D. Are allowed if lead covered
300.3(A)

## Slide 184
A. ½ inch
Holes bored in wood structures may not have the edge of the hole closer than ____inches to the edge of the member.
B. ¾ inch
C. 1 inch
Your answer would be D. 1 ¼ inch
What code reference are we going to use?
D. 1 ¼ inch
300.4

## Slide 185
A. Install grommets in the holes
When installing cabling through holes in metal framing you must?
B. Use wire protectors installed on the wiring
C. Insulate the metal framing member
Your answer would be A. Install grommets in the holes
What code reference are we going to use?
D. Never use non-metal wiring covering with metal studs
330.4(B)

## Slide 186
A. The insulation ratings on all conductors are all for the highest voltage applied
Conductors of a low voltage circuit can occupy the same space as line voltage conductors if?
B. The low voltage conductors are identified in the enclosure
C. There is at least 1” of non-conductive material in between the conductors
Your answer would be A. The insulation ratings on all conductors are all for the highest voltage applied
What code reference are we going to use?
D. Approved by the AHJ for special circumstances
300.3(C)

## Slide 187
A. By the suspended ceiling grid T’s
Cables installed above suspended ceilings shall be supported?
B. By the ceiling grid support wires
C. By a cable tray only
Your answer would be D. By separate support wire installed by electrical personnel
What code reference are we going to use?
D. By separate support wire installed by electrical personnel
300.11

## Slide 188
A. Buried at least 6 inches
Underground wiring for low voltage landscape lighting must be?
B. Buried per manufacturer’s instructions
C. Installed in PVC
Your answer would be B. Buried per manufacturer’s instructions
What code reference are we going to use?
D. Spliced in waterproof splices
300.5

## Slide 189
A. The raceway to be filled to 85%
Raceways for conductors or cables must be large enough to permit?
B. The installation and removal of conductors without damage
C. Additional wiring to be installed later
Your answer would be B. The installation and removal of conductors without damage
What code reference are we going to use?
D. Pulling in conductors without friction on the conductors
300.17

## Slide 190
A. Required at all splices and terminations
Electrical Boxes are?
B. Not required for communication circuits
C. Needed when conductor ampacity changes
Your answer would be B. Not required for communication circuits
What code reference are we going to use?
D. Listed as to the maximum voltage rating of the box
300.15

## Slide 191
A. More current capability
CI cables are used to ____for power limited circuits
B. Integrity of the circuit voltage
C. Circuit survivability in case of a fire
Your answer would be C. Circuit survivability in case of fire
What code reference are we going to use?
D. Circuit integration of systems
725.2

## Slide 192
A. THW
Conductors with ____ marked on the insulation are NOT approved for use in a wet location.
B. THHW
C. THHN
Your answer would be C. Conductors with THHN insulation are approved for use in dry and damp locations only.
What code reference are we going to use?
D. THWN
310.104(A)

## Slide 193
A. 1/0 AWG
A one-family dwelling unit with a demand load of 200 amperes is supplied with a 120/240 volt, single-phase, electrical system from the local utility company. What is the MINIMUM size aluminum THW conductors
required for use as service-entrance conductors for
this residence?
B. 4/0 AWG
C. 3/0 AWG
Your answer would be B. Section 310.15(B)(7) permits Table 310.15(B)(7) to be used for sizing 120/240 volt, single-phase, service-entrance conductors for a one-family dwelling. Table 310.15(B)(7) indicates size 4/0 AWG THW aluminum conductors with an allowable ampacity of 200 amperes should be selected for this dwelling.
What code reference are we going to use?
D. 2/0 AWG
310.15 (B)(7)

## Slide 194
A. 625 amperes
Where a 150 kVA, single-phase transformer having a secondary voltage of 120/240 is installed at a multi-family dwelling, the full-load current rating, in amperes, of the secondary is______?
B. 265 amperes
C. 526 amperes
Your answer would be A. To find the full-load current rating of the single-phase transformer apply the single-phase current formula:
I = (150 kVA x 1000) / 240 = 15000 / 240 = 625 amperes
D. 1250 amperes